DATA SHEET

LG Programmable Logic Controller

GLOFA-GM 6 CPU Module

GM6-CPUA

GM6-CPUB

GM6-CPUC

LG Industrial Systems

● Beijing Branch             	● Bangkok Branch

LG Industrial Systems 		LG Industrial Systems (Thailand)

Elevator Co., Ltd. 		Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch          	● Chicago Branch

LG Industrial Systems de 	LG Industrial Systems Co., Ltd.

Colombia S.A.    		Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch              	● Hanoi Branch

Dalian LG Industrial Systems 	LG Industrial Systems Co., Ltd.

Co., Ltd.      		Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch         	● Shanghai Branch

LG Industrial Systems (HK) Ltd.   Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch          	● Taipei Branch

LG Industrial Systems Co., Ltd.    LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

702005592

Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming software) | 702005047 |
| GLOFA GMWIN (Instruction & programming) | 702005058 |
| GLOFA GM6 User’s manual | 702005581 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the GLOFA-GM6 CPU module. For safety precautions on the PLC system, see the GLOFA GM6 User’s manual.

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard..

!

## Warning

If not provided with proper prevention, it can cause death, fatal injury or considerable loss of property

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

!

Caution

However, a precaution followed with ‘Caution’ can also result in serious conditions.

Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it. Keep this manual handy for your quick reference in necessary.

 Design Precautions

Caution

Don not run I/O signal lines near to high voltage line or power line.

Separate them as 100mm or more as possible. Otherwise, noise can cause module malfunction.

 Installation Precautions

Caution

Operate the PLC in the environment conditions given in the general specifications..

If operated in other environment not specified in the general specifications, it can cause an electric shock, a fire, malfunction or damage or degradation of the module.

Make sure the module fixing projections is inserted into the module fixing hole and fixed.

Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

## Caution

Make sure that FG the terminal is grounded with class 3 grounding which is dedicated to the PLC. Otherwise, it can cause disorder or malfunction of PLC.

PLC

Others

< Best >

PLC

Others

PLC

Others

< Good >

< Bad >

 Before the PLC wiring, be sure to check the rated voltage and terminal arrangement for the module and observe them correctly. If a different power, not of the rated voltage, is applied or wrong wiring is provided, it can cause a fire or disorder of the module.

Drive the terminal screws firmly to the defined torque. If loosely driven, it can cause short circuit, a fire or malfunction.

Be careful that any foreign matter like wire scraps should not enter into the module. It can cause a fire, disorder or malfunction.

 Test RUN and maintenance precautions

Warning

Do not contact the terminals while the power is applied. It can cause malfunction.

When cleaning or driving a terminal screw, perform them after the power has been turned off.

Caution

Do not separate the module from the printed circuit board, or do not remodel the module. They can cause disorder, malfunction, damage of the module or a fire. When mounting or dismounting the module, perform them after the power has been turned off.

Do not change battery while power is off. It can cause loss of data.

 Waste Disposal Precaution

Caution

When disposing the module, do it as an industrial waste.

1. Introduction

This data sheet provides brief information about characteristics, configuration, and usage of GLOFA PLC GM6 CPU (GM6-CPUA, GM6-CPUB, GM6-CPUC) module.

2. General Specifications

| No | Item | Specifications |  |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ (32 ~ 131°F) |  |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ (-13 ~ 158°F) |  |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency |  | Acceleration |  | Amplitude |  | Sweep count |  |
|  |  | 10≤f∠57 Hz |  | - |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz |  | 9.8㎨ {1G} |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |  |
|  |  | Frequency |  | Acceleration |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz |  | - |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz |  | 4.9㎨{0.5G} |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse ( 3 times in each of X, Y and Z directions ) |  |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  |  |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient burst noise | Severity Level |  | All power modules | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage |  | 2 kV | 1 kV | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |  |

3. Performance Specifications

| Items |  |  | Specifications |  | Remark |
| --- | --- | --- | --- | --- | --- |
|  |  |  | GM6-CPUA |  |  |
| Operation method |  |  | Cyclic operation of stored program Interrupt task operation |  |  |
| I/O control method |  |  | Scan synchronized batch processing method (Refresh method) |  |  |
| Programming Language |  |  | Ladder Diagram (LD) Instruction List ,(IL) Sequential Function Chart (SFC) |  |  |
| Numbers of instructions | Operator |  | LD:13,IL:21 |  |  |
|  | Basic function |  | 194 |  |  |
|  | Basic function block |  | 11 |  |  |
|  | Special function block |  | Each special modules have their own special function blocks. |  |  |
| Operator |  |  | 0.5㎲/step |  |  |
| Program memory capacity |  |  | 68 Kbyte (17 Kstep) |  |  |
| Max. I/O points |  |  | 256 points |  |  |
| Data memory | Direct variable area |  | 2 ∼ 8 Kbyte |  |  |
|  | Symbolic variable area |  | 30 Kbyte – Direct variable area |  |  |
| Timer |  | ·No limitation in points (1 timer occupies 20 byte of symbolic variable area) ·Time range :0.0.1∼4,294,967.29 sec (1,193hours) |  |  |  |
| Counter |  | ·No limitation in points (1 point occupies 20 byte of symbolic variable area) ·Counting range :－32,768∼＋32,767 |  |  |  |
| Numbers of program block |  |  | 100 |  |  |
| Initialization programs |  |  | 1(_INIT) |  |  |
| Task program |  |  | Time driven task | 8 | Max. 8 tasks (Total) |
|  |  |  | External interrupt task | 8 |  |
|  |  |  | Internal task | 8 |  |
| Operation mode |  |  | RUN,STOP,PAUSE,DEBUG |  |  |
| Restart mode |  |  | Cold, Warm |  |  |
| Self-diagnostic functions |  |  | Watch dog timer, memory error detection, I/O error detection, Battery error detection, etc. |  |  |
| Internal power consumption |  |  | 0.15A |  |  |
| Weight (㎏) |  |  | 0.11 |  |  |

4. Operation Processing Method

1) Cyclic operation

A PLC program is sequentially executed from the first step to the last step, which is called scan. This sequential processing is called cyclic operation. Cyclic operation of the PLC continues as long as conditions do not change for interrupt processing during program execution.

Stages                                 Processing

Operation Start

·Stage for the start of a scan processing. It is executed only

Initialization             one time when the power is applied or reset is executed. It

executes the following process.

▶I/O module reset    ▶Self diagnosis

▶Data clear          ▶I/O module address allocation

·Read input module conditions and store it into the input image

Input image area refresh       area before operation processing of a program.

Program operation        ·Program is sequentially executed from the first step to the last

The start of program         step.

The end of program

·The contents stored in the output image area is output to output

Output image area refresh      modules when operation processing of a program is finished

·Stage for return processing after the CPU module has finished

END processing             1 scan. The following processing are executed..

▶Self-diagnosis

▶Change of the present values of timer and counter, etc.

▶Check the status of mode setting switch

2) Time driven interrupt operation method

In time driven interrupt operation method, operations are processed not repeatedly but at every preset interval. In the GM6 CPU module, interval can be set to between 0.01 ~ 4294967.29 second. This operation is used to process operation with a constant cycle

3) Event driven interrupt operation method

If a situation occurs which is requested to be urgently processed during execution of a PLC program, this operation method processes immediately the operation which corresponds to interrupt program. The signal which informs those urgent conditions to the CPU module is called interrupt signal. The GM6 CPU module has two kind of interrupt operation methods, which are internal and external interrupt signal methods.

5. Parts Name and Descriptions

The following describes the names and functions of parts of the CPU module.

| GM6-CPUA GM6-CPUA ① ② ③ ④ ⑤ |  |  |
| --- | --- | --- |
| No. | Name | Function |
| 1 | RUN LED | Indicates the operation status of the CPU module.  On : when the CPU module operates with the mode setting switch in the local or remote RUN state.  Off : when the followings occur The voltage is not normally supplied to the CPU module. The mode setting switch is in the STOP or PAU/REM state. An error which makes operation stop is detected. |
| 2 | STOP LED |  On : when the mode setting switch is in the local or remote STOP state.  Off : when the followings occur The mode setting switch is in the local RUN or local PAUSE state. The operation state is in the RUM/PAUSE/DEBUG state.  Flickering : when an error is detected by self-diagnosis during operation. |
| 3 | Mode setting switch | Sets the operation mode of the CPU module. .  RUN : Program operation is executed.  STOP : Program operation is temporarily stopped.  PAU/REM : PAUSE : Program operation is temporarily stopped. REMOTE: Used for the remote operation |
| 4 | RS-232C connector | 9-pin connector for GMWIN and Cnet (RS-232C) |
| 5 | RS-422 and HSC terminal (B/C type only) | Pin No RS-422/485 High Speed Counter 1 RDA A phase input 2 RDB B phase input 3 SDA A/B phase common 4 SDB Preset input (+24V) 5 S.G Preset common (0V) |

6. Using The User Program in Flash Memory

This chapter describes how to store and operate user program with the flash memory .

Flash memory is used to store a user program and installed in PLC.

1) Structure

Dip switch for operation

Flash memory

Read / Write is available to flash memory in accordance with selection of DIP switch.

| Selection of DIP switch for flash memory | Operation |
| --- | --- |
| ON | PLC is operated by the program in flash memory when power on or PLC reset. |
| ON | PLC recognize that no program is in flash memory. |

( Caution : Lower switch should be at the off position. )

User program can be written to flash memory at the PLC stop mode and then the selection of switch is ignored.

7. Power Supply Modules

This chapter describes type and specifications of the power supply modules

- Selection of power supply module

Selection of the power supply module is determined by the total current consumption of digital input modules, special modules and communications modules, etc. whose powers are supplied by the power supply module.

If total load overrun the rated output capacity, the system will not normally operate. When configuring a system, select a power supply module with due consideration of current consumption of each module.

Current Consumption of GM6 Series Modules                          (Unit:㎃)

| Module | Model Name | Current Consumption | Module | Model Name | Current Consumption |
| --- | --- | --- | --- | --- | --- |
| CPU | GM6-CPUA | 170 | Transistor Output | G6Q-TR4A | 140 |
|  | GM6-CPUB | 210 |  | G6Q-TR4B | 145 |
|  | GM6-CPUC | 170 | A/D Module | G6F-AD2A | 50 |
| DC 12/24V Input | G6I-D21A | 40 | D/A Module | G6F-DA2V | 50 |
|  | G6I-D22A | 70 |  | G6F-DA2I | 50 |
|  | G6I-D22B | 70 | High Speed Counter | G6F-HSCA | 220 |
|  | G6I-D24A | 75 | Positioning module | G6F-POPA | 345 |
|  | G6I-D24B | 75 | Computer link module (Cnet) | G6L-CUEB | 140 |
| AC110V Input | G6I-A11A | 35 |  | G6L-CUEC | 180 |
| AC220V Input | G6I-A21A | 35 | Fnet I/F module | G6L-FUEA | 215 |
| Relay Output | G6Q-RY1A | 210 |  | G6L-RBEA | 215 |
|  | G6Q-RY2A | 400 | Dnet I/F module | G6L-DUEA | 220 |
| Triac Output | G6Q-SS1A | 190 |  | G6L-DSIA | 155 |
| Transistor Output | G6Q-TR2A | 180 |  | G6L-DSQA | 240 |
|  | G6Q-TR2B | 170 |  |  |  |

- Specification

| Item |  | GM6-PAFA | GM6-PAFB | GM6-PDFA | GM6-PD3A |
| --- | --- | --- | --- | --- | --- |
| Input | Voltage | AC100 ~ 240V (85∼264V) |  | DC12 ~ 24V | DC24V |
|  | Frequency | 50/60Hz(47∼63 Hz) |  | - |  |
|  | Current | 0.7/0.35A |  | 0.7 / 1.8A | 0.7 / 1.2A |
|  | Inrush Current | 30A or less |  | 40A or less |  |
|  | Efficiency | 65% or more (Normal load) |  | 60% or more (normal load) |  |
|  | Fuse Type | 250VAC / 2A |  | 250VAC/ 3A |  |
|  | Dropout Tolerance | 20ms or less |  | 1ms or less |  |
| Output | Voltage | DC5V DC24V | DC5V DC+15V DC-15V | DC5V | DC5V |
|  | Current | DC5V:2A DC24V:0.3A | DC5V:2A DC+15V:0.5A DC-15V:0.2A | DC5V : 2A | DC5V : 2A |
|  | Over-current Protection | DC5V:2.2A DC24V:0.33A | DC5V:2.2A DC+15V:0.55A DC-15V:0.22A | DC5V : 2.2A | DC5V : 2.2A |
| LED Indication |  | On : The output voltage is normal |  |  |  |
| Allowable Cable Specification |  | 0.75∼2mm² |  |  |  |
| Weight (kg) |  | 0.32 |  |  |  |

- Names of Parts

①

②

⑤

③

④

| No. | Name | Description |
| --- | --- | --- |
| 1 | Power LED | ＊The LED indicator for DC5V power |
| 2 | Power Input Terminal | ＊The terminal to connect 100~240VAC power |
| 3 | LG Terminal | ＊Line ground |
| 4 | FG Terminal | ＊Frame ground |
| 5 | DC24V Terminal DC24VGTerminal | ＊Supply DC24V power to the other modules (GM6-PAFA) ＊No Connection(GM6-PAFB, GM6-PDFA, GM6-PD3A) |

8. Mounting and Dismounting of Module

The following explains that how to mount/dismount various module to the base.

Locking part

for hook

Locking Hook

1) Mounting a module

- Insert the module to mounting slot along sliding guide.

Sliding Guide

Locking Hook

Locking part for hook

- Check that the module is firmly mounted onto the base.

2) Dismounting a module

- First, push the locked hook (①) and pull the module with direction of arrow (②).

Locking part for hook

Sliding Guide

Locking part for hook

Locking Hook

9. PID control function (GM6-CPUB / GM6-CPUC)

10. RS-422/485 master function (GM6-CPUB)

GM6-CPUB and GM6-CPUC module include PID (Proportional Integral Differential) function, and no external PID module is required.

- Characteristics of GM6 PID function

- PID function is included in the CPU module, and no PID module is required.

- User can select forward or reverse operation.

- P, PI, PID or On/Off operation modes are available.

- Manual output (user-defined output) is available.

PID operation

D/A conversion

Actuator

A/D conversion

SV

DV

PV

Sampling time can be varied for flexibility of control system.

- Function blocks for PID control

GMWIN provides 2 functions blocks as following table (version 3.2 or later)

| No. | Name | Description |
| --- | --- | --- |
| 1 | PID6CAL | Perform PID operation |
| 2 | PID6AT | Perform auto tuning operation |

- Introduction

The GM6-CPUB module has RS-422/485 master function and can operate as master station of 1:N network.

- Functions

- User can define a data access block on I/Q/M area and set time-out value at each blocks. The maximum size of block is 64 words.

- Maximum station number is 32 stations.

- According to the parameter setting, the operation mode and error code of slave stations is stored at the relevant flag.

- The communication status can be monitored with the monitoring function of GMWIN software.

11. Built-in high speed counter (GM6-CPUC)

- Introduction

The GM6-CPUC module includes a built-in high speed counter, and it can count a fast pulse input that are generated by encoder or pulse generator.

The built-in HSC has following functions;

- 3 counter functions as followings

- 1-phase up / down counter 	: Up / down is selected by user program

- 1-phase up / down counter 	: Up / down is selected by external B phase input

- 2-phase up / down counter 	: Up / down is automatically selected by the phase difference between phase A and B.

- Multiplication (1, 2, or 4) with 2-phase counter

- 2-phase pulse input multiplied by one	: Counts the pulse at the leading edge of phase A.

- 2-phase pulse input multiplied by two	: Counts the pulse at the leading / falling edge of phase A.

- 2-phase pulse input multiplied by four	: Counts the pulse at the leading / falling edge of phase A and B

- Performance specifications

| Items |  | Specifications |
| --- | --- | --- |
| Input signal | Types | Phase A, Phase B, Preset |
|  | Rated level | 24VDC (13mA) |
|  | Signal type | Voltage input |
| Counting range |  | 0 ~ 16,777,215 (Binary 24 bits) |
| Max. counting speed |  | 50k pps |
| Up / Down selection | 1-phase | Sequence program or B-phase input |
|  | 2-phase | Auto-select by phase difference of phase A and B |
| Multiplication |  | 1, 2, or 4 |
| Preset input |  | Sequence program or external preset input |

12. Troubleshooting

- Error code

| Error code | Cause | Corrective Action | Operation status | STOP LED Flickering cycle | Diagnosis time | Re-start mode |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | OS ROM error | Contact the service center if it reactively occurs when the power is re-applied. | Defect | 0.4 sec | When power is applied | - |
| 3 | OS ROM error | " | Defect | 0.4 sec | When power is applied | - |
| 4 | RTC fault | " | Defect | 0.4 sec | When power is applied | - |
| 5 | Dedicated processor fault | " | Defect | 0.4 sec | When power is applied | - |
| 6 | Program memory fault | " | Defect | 0.4 sec | When power is applied | - |
| 7 | Data memory fault | " | Defect | 0.4 sec | When power is applied | - |
| 10 | Watch dog error due to OS program congestion | RE-apply the power | Reset | 0.4 sec | During run | Cold |
| 20 | Program memory backup error | Replace the battery if it has error check the program after cc-loading it, and if an error is detected replace the CPU module | STOP | 0.4 sec | When power is applied | Cold |
| 21 | Memory module defect | Check and correct the memory module mounting condition Re-apply the power and if an error occurs, replace the memory module | STOP | 0.4 sec | When power is applied | Cold |
| 22 | Memory module program fault | Correct the memory module program and re-operate the system | STOP | 0.4 sec | Change into the RUN mode | Cold |
| 23 | An normal program | Re-load the program and start it | STOP | 0.4 sec | Change into the RUN mode | Cold |
| 30 | Inconsistency between the specified modules by parameters and the loaded modules | Module type inconsistency error Refer to the flags(_IO_TYER,_IO_ DEER_N, _IO_TYER [n]) and correct the wrong slot, and re-start the system | STOP | 0.4 sec | Change into the RUN mode | Cold |
| 31 | Module dismounting or additional mounting during run | Module mounting/ dismounting error Refer to the flags(_IO_DEER,_IO_ DEER_N, IO_DEER [n]) and correct the in corrective slot, and re-start the system | STOP | 0.4 sec | When scan completes | Cold |
| 32 | Fuse disconnection during run | Fuse disconnection error Refer to the flags(_FUSE_ER,_FUSE _ER_N, FUSE_ER[n]) and correct the in corrective slot, and re-start the system | STOP | 0.4 sec | When scan completes | Cold |
| 33 | Abnormal I/D module data access during run | I/O module read/ write error Refer to the flags(IO_RWER, _IP_RWER_N, _IO_RWER [n]) and restart the system | STOP | 0.4 sec | When scan completes During execution of program | cold |
| 34 | Abnormal special/ link module data access during run | Special/ link module interface error Refer to the flags(_SP_IFER,_IP_ IFER_N,_IP_IFER [n]) and restart the system | STOP | 0.4 sec | When power is applied When scan completes During execution of program | cold |
| 40 | During run, Scan time over than the scan delay time specified by parameters | Check the scan delay time specified by parameters and correct the parameters or the program, and then re-start the program | STOP | 0.4 sec | During execution of program | cold |
| 41 | Unreadable instructions in the user program | Re-load the program and re-start it | STOP | 0.4 sec | During execution of program | cold |
| 50 | External device fatal error | Refer to the external device fatal error flags(_ANNUN_ER,_ANC_ERR[n]) and correct the fault devices and then re-start the system | STOP | 0.4 sec | When scan completes | cold |
| 60 | The 'E-STOP' function has been executed | Correct the program so that the error elements that invoked the 'E_STOP' function can be eliminated in the program and re-start the system(Cold re-start) | STOP | - | During execution of program | cold |
| 100 | Communications module configuration error | If the number of computer 4communications module is included, then adjust the maximum number with in 8 | STOP | 0.4 sec | When power is applied | cold |
| 101 | Special/ Communications module initialization failure | Adjust the number of high speed communications modules loaded | STOP | 0.4 sec | When power is applied | cold |
| 500 | Data memory backup error | If the battery has no error | RUN | - | When power is applied | cold |
| 501 | RTC data error | If the battery has no error, re-set the time using the GMWIN | RUN | 2 sec | When power is applied When scan completes | - |
| 502 | Lower battery voltage | Replace the battery which the power is being applied. | RUN | 4 sec | When power is applied When scan completes | - |

13. Dimension (mm)

12. Troubleshooting

◆ Power Supply Module                        ◆ CPU & I/O Module

GM6-CPUA

45

100

100

45

110

GM6-CPUA

100

35

110

100

35

110

110

92

62

4 – ψ4.5

A

B

C

D

E

◆ Base

| Slot Type | A | B | C | D | E |
| --- | --- | --- | --- | --- | --- |
| 4 slots | 230.5 | 244 | 92 | 110 | 62 |
| 6 slots | 300.5 | 314 | 92 | 110 | 62 |
| 8 slots | 370.5 | 384 | 92 | 110 | 62 |