Data Sheet

LG Programmable Logic Controller

FieldBus Network Module

GLOFA-GM  G6L-FUEA

LG Industrial Systems

● Beijing Branch             	● Bangkok Branch

LG Industrial Systems 		LG Industrial Systems (Thailand)

Elevator Co., Ltd. 		Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch          	● Chicago Branch

LG Industrial Systems de 	LG Industrial Systems Co., Ltd.

Colombia S.A.    		Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch              	● Hanoi Branch

Dalian LG Industrial Systems 	LG Industrial Systems Co., Ltd.

Co., Ltd.      		Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch         	● Shanghai Branch

LG Industrial Systems (HK) Ltd.   Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch          	● Taipei Branch

LG Industrial Systems Co., Ltd.    LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

702005649

Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming software) | 702005047 |
| GLOFA GM (Instruction & Programming) | 702005058 |
| GLOFA GM6 (User’s manual) | 702005581 |
| GLOFA GM Fnet/Mnet (User’s manual) | 702005070 |

| Name | GLOFA-GM G6L-FUEA Data Sheet |
| --- | --- |
| Code | 702005649 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the GLOFA G6L-FUEA module.

For safety precautions on the PLC system, please see the GLOFA GM6 user’s manual.

If not provided with proper prevention, it can cause death, fatal injury or considerable loss or property

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

WARNING

!

CAUTION

!

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard.

However, a precaution followed with    CAUTION  can also result in serious condition. Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it.

Keep this manual handy for your quick reference in necessary.

 Design Precaution

CAUTION

Do not run I/O signal lines near to high voltage line or power line. Separate them as 100mm or more as possible. Otherwise, noise can cause module malfunction

 Installation Precaution

CAUTION

Operate the PLC in the environment conditions given in the general specifications

If the PLC is operated in other environment not specified in the general specification, it can cause an electric shock, a fire, malfunction or damage or degradation of the module.

Make sure the module fixing projections is inserted into the module fixing hole and fixed.

Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

CAUTION

Drive the terminal screws firmly to the defined torque. If loosely driven, it can cause short circuit, fire or malfunction.

Be careful that any foreign matter like wire scraps should not enter into the module. It can cause a fire, disorder or malfunction.

 Test RUN and Maintenance Precautions

WARNING

Do not contact the terminals while the power is applied. It can cause malfunction.

When cleaning or driving terminal screws, perform them after the power has been turned off.

Do not perform works while the power is applied. It can cause disorder or malfunction.

CAUTION

Do not separate the PCB from the case of module, or do not remodel the module. They can cause disorder, malfunction, damage of the module or a fire.

 Waste Disposal Precautions

CAUTION

When disposing the module, do it as an industrial waste.

1. Introduction

This data sheet contains the brief information about the characteristics, configurations, and operating of GLOFA PLC Fnet (G6L-FUEA) module.

2. General Specifications

| No. | ###### Item | Specification |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency | Acceleration |  | Amplitude |  | Sweep count | IEC 1131-2 |
|  |  | 10≤f∠57 Hz | - |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz | 9.8㎨ {1G} |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz | - |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz | 4.9㎨{0.5G} |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient burst noise | Severity Level | All power modules | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage | 2 kV | 1 kV | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |

3. Performance Specifications

| Model Item | G6L-FUEA |
| --- | --- |
| Dropout Tolerance | 20ms |
| Transfer rate | 1Mbps |
| Comm. Method | Half duplex bit serial method |
| Synchronization | Frame synchronous method |
| Transmission method | Bus type |
| Max. cable length | 750m |
| No. of station | Up to 64 stations |
| Modulation | Manchester Biphase-L |
| Error detect | CRC-CCITT and Time Over |
| Connector type | 9-pin plug type |
| Cable type | Twisted pair cable |
| Max. link points | 3,840 Word |
| Max. transfer points | 1,920 Word |
| Max. No. of block | 64 blocks |
| Max. points per 1 block | 60 Word |
| Current consumption | 182 mA |
| Weight | 102 g |

4. Cable Specifications

Twisted pair cable

| Type | LIREV-AMESB 2*1.0mm 18AWG | Structure |
| --- | --- | --- |
| Manufacturer | LG Cable | Conductor Insulator |
| Cable type | Twisted pair shielded cable |  |
| Impedance | 21.8Ω/㎞ |  |
| Withstanding voltage | 500 V/Min (DC) |  |
| Insulation resistance Ground line | 1,000㏁/㎞ or more |  |
| Capacity | 45 ㎊/m or less (1㏀) |  |
| Characteristic impedance | 120±12Ω(10㎒) |  |
| Core | 2 Cores |  |

5. Connection of Communication Cable

Cable for electric network connection uses only No. 6 and No.7 of the connector pins. They should be connected with the pin has the same pin number. Each body of connector should be connected with shield wire.

Twisted pair cable

6

7

6

7

6

7

6

7

Shield wire

Module A                   Module B

6. Terminal Resistance

Pin 7

Pin

6

Resistor

9-pin socket type

 Resistor : 110, 1/2W

 Connection : Pin 6 and 7

 Attach 110, 1/2W resistor of spare parts to the connectors of both end of network.

 Connector case should not be connected with resistor.

7. Parts Name and Description

G6L-FUEA

RUN

LAS

TOKEN

TX/RX       FAULT

G6L-FUEA

MODE

ON-LINE

TEST1

TEST2

G6L-FUEA

CON1

CON2

| Item | Description |
| --- | --- |
| ① LED | RUN : Indicates the status of communication of PLC ( Normal : ON) LAS : Turn on when the module is performing LAS function. TOKEN : Turn on when the module has token. TX/RX : Turn on when the module is transmitting/receiving FAULT : Flickers when comm. error occurred. |
| ② Mode setting | 0 : ON-LINE normal communication 1 : Communication test mode 1 2 : Communication test mode 2 |
| ③ Station No. setting (Inside of module) | Station number (0~63), Set in decimal Example ) X10 = 4, X1 = 7 4 X10 + 7 X1 = Station No. 47 |
| ④ Connector | CON1/2 : FieldBus cable connector (9-pin plug type) |

①

②

③

④

8. Fnet System Configuration

GM1 multi-CPU, GM2 system

GM3 remote base

GM4 remote base

GM6 system

GMR Redundancy system

GM4 system

G0L-FUEA

# Active coupler (G0L-FACA)

Repeater(G0L-FREA)  Optical/electric converter(G0L-FOEA)

GM3 remote expansion base

GM4 remote expansion base

: Electrical (twisted pair) cable            : Optical fiber cable

9. LED Indication for Error Status

| Error type | LED Status | Description |
| --- | --- | --- |
| During Power is On |  | Self diagnosis of internal memory 1 |
|  |  | Self diagnosis of internal memory 2 |
|  |  | Self diagnosis of communication |
|  |  | Diagnosis of interface with CPU |
| Normal Communication |  | Module is not LAS |
|  |  | Module is LAS |
| Hardware Error |  | Error in self diagnosis of internal memory 1 |
|  |  | Error in self diagnosis of internal memory 2 |
|  |  | Error in self diagnosis of communication |
|  |  | Error in diagnosis of interface chip |
|  |  | Error in diagnosis of interface RAM |
|  |  | Error 1 in diagnosis of CPU interface |
|  |  | Error 2 in diagnosis of CPU interface |
|  |  | Error 3 in diagnosis of CPU interface |
| System Operation Error |  | System error during operation |
| Abnormal Communi-cation |  | Error in network configuration status |
|  |  | Duplicated station No, abnormal terminal resistor |
|  |  | Cable cut off or short |
|  |  | Specified length of cable is not proper or hardware error of the module |
|  |  | Error of network configuration |
| Interface Error |  | Interface error (stopped) of LAS |
|  |  | Interface error (stopped) of non LAS |
| Unrecoverable Error |  | Hardware error of communication module |

※ LED position follows the sequence of RUN, LAS, TOKEN, TX/RX, and FAULT from left side.

LED On                                               LED off

Flickering with 1 second interval

Flickering with irregular interval or LED off

Flickering with irregular interval

10. Status Code of Function Block (Error List)

① Error received from the communication module

| Error No. (Decimal) | Description |
| --- | --- |
| 0 | Normal (No error) |
| 1 | Physical layer error of link side (Tx/Rx is impossible) - Self-station error, other station’s power off, station No. error, etc. |
| 4 | Data type mismatch |
| 8 | Access denied to remote object |
| 10 | Response waiting time over(Time out error) |
| 11 | Structure error |
| 12 | Abort (disconnected by serious error) |
| 13 | Reject (type mismatch with MMS or error caused by noise) |
| 33 | Variable identifier is not found (Access variable setting error) |
| 34 | Address error |
| 50 | Response error (response is different with required format or other station’s CPU error |

② Status values indicated by CPU

| Error No. (Decimal) | Description |
| --- | --- |
| 16 | Position error of communication module |
| 17 | Initialization error of communication module mounted in SLOT_NO |
| 18 | Input parameter setting error |
| 19 | Variable length error |
| 20 | Improper response is received from other station |
| 21 | No response during specified waiting time (Time our error) |

11. Maintenance

Perform routine check and regular check to maintain the best status of the communication module.

- Daily check

| Check Item |  | Contents | Decision Criteria |
| --- | --- | --- | --- |
| Cable connection |  | Release of cable | No released cable |
| Module connection |  | Release of screw | No released screw |
| LED | RUN LED | Flicker check | Flickering (Off means interface with CPU is cut off) |
|  | LAS LED | Light on check | LED of only one module among modules of entire network should be lighted. (It means abnormal configuration of network that two or more LED is on.) |
|  | TOKEN LED | Flicker check | Light off means abnormal (Duplicated station or cable error) |
|  | TX/RX LED | Flicker check | Light off means abnormal (Hardware error of module) |
|  | FAULT LED | Light off check | Regular flickering : system error Irregular flickering : communication error |

- Regular check

Check following items once or twice per six months, and perform relevant action.

| Check Item |  | How to check | Decision Criteria |
| --- | --- | --- | --- |
| Ambient environment | Temperature | Thermometer/Hydrometer | 0 ~ 55 C |
|  | Humidity |  | 5 ~ 95 %RH |
|  | Atmosphere | Check corrosive gas | No corrosive gas |
| Module status | Release | Shake the module | No release |
|  | Dust or foreign matter | Visual inspection | No dust of foreign matter |
| Connection status | Release of screw | Tighten with a driver | No release |
|  | Compression terminals | Visual inspection | Proper gap |
|  | Connector | Visual inspection | No release |
| Power voltage check |  | Check voltage between terminals | AC 85 ~ 132 [V] AC 170 ~ 264 [V] |

12. Handling Instructions

1)   Including self-station, all modules in the whole network must have different high speed link station number. If there is any duplicated station number, normal communication is impossible.

- Set mode switch at ‘On-Line’ mode during normal communication. If turn on the module with ‘Test 1’ mode while other stations of network are communicating, it can cause serious problem on communication.

- Use cable complied with specification of this data sheet. Otherwise, it can cause serious communication error.

- Make sure that communication cable connector fastened firmly. Otherwise, it can cause serious communication error.

- Improper cable connection (snarled cable, redundant connection, etc) can cause communication error.

- Do not place communication cable near power cable or inductive noise source.

- Make sure that shield wire is connected to the metal case of 9-pin connector.

- Do not mount or dismount module while power is applied to the module. Therefore, turn off the module before repairing or replacement.

- Change of station number or mode switch setting will not take effect before power is re-applied.

13. Dimension

G6L-FUEA

unit : mm

RUN

## LAS

TOKEN

TX/RX          FAULT

# G6L-FUEA

G6L-FUEA

#### CON1

#### CON2

MODE

ON-LINE

TEST1

TEST2

×10   ×1

CON1

CON2

38

110

35

G6L-FUEA

90