DATA SHEET

LG Programmable Logic Controller

Digital to Analog Conversion Module

GLFA G6F-DA2V/G6F-DA2I

LG Industrial Systems

● Beijing Branch                   ● Bangkok Branch

LG Industrial Systems Elevator Co., Ltd.     LG Industrial Systems (Thailand) Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch                   ● Chicago Branch

LG Industrial Systems de Colombia S.A.    LG Industrial Systems Co., Ltd. Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch                    ● Hanoi Branch

Dalian LG Industrial Systems Co., Ltd.      LG Industrial Systems Co., Ltd. Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch                ● Shanghai Branch

LG Industrial Systems (HK) Ltd.           Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch                 ● Taipei Branch

LG Industrial Systems Co., Ltd.            LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

###### Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or

start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming Software) | 702005047 |
| GLOFA GM (Instruction & programming) | 702005058 |
| GLOFA-GM6 | 702005592 |
| GLOFA G6F-DA2V / G6F-DA2I | 702005774 |

| Name | G6F-DA2V/G6F-DA2I Datasheet |
| --- | --- |
| Code | 702005730 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the G6F-DA2V and G6F-DA2I.

For safety precautions on the PLC system, see the GLOFA GM6 User’s Manuals.

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard.

WARNING

!

If not provided with proper prevention, it can cause death, fatal injury or considerable loss of property.

CAUTION

!

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

CAUTION

!

However, a precaution followed with                can also result in serious conditions.

Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it. Keep this manual handy for your quick reference in necessary.

WARNING

!

 Design Precautions

▶ Design a safety circuit in the outside of the PLC for system safety in case of disorder of the

external power or PLC module body. Otherwise, it can cause injury due to wrong output or

malfunction.

- The following shows analog output states.

| Channel Setting State | Channel Specification |  |
| --- | --- | --- |
|  | Used | Unused |
| PLC CPU in RUN state | D/A Conversion value is output | Voltage : 0V Current : 4㎃ |
| PLC CPU in STOP state | Voltage : 0V Current : 4㎃ |  |
| PLC CPU in Error state | Previous value |  |

2) Sometimes, fault of output device or internal circuit can make output abnormal. Design a

supervising circuit in the outside for output signals which can cause serious accidents

CAUTION

!

▶Do not run I/O signal lines near to high voltage line or power line.

Separate them as 100 mm or more as possible. Otherwise, noise can cause module

malfunction.

CAUTION

!

 Installation Precautions

▶Operate the PLC in the environment conditions given in the general specifications.

▶If operated in other environment not specified in the general specifications, it can

cause an electric shock, a fire, malfunction or damage or degradation of the module.

▶Make sure the module fixing pro-jections is inserted into the module fixing hole and fixed.

▶Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

CAUTION

!

▶When grounding a FG terminal, be sure to provide class 3 grounding which is dedicated to

the PLC.

▶Before the PLC wiring, be sure to check the rated voltage and terminal arrangement for the

module and observe them correctly. If a different power, not of the rated voltage, is applied or

wrong wiring is provided, it can cause a fire or disorder of the nodule.

▶Drive the terminal screws firmly to the defined torque.

If loosely driven, it can cause short circuit, a fire or malfunction.

▶Be careful that any foreign matter like wire scraps should not enter into the module.

It can cause a fire, disorder or malfunction.

WARNING

!

 Test RUN and Maintenance Precautions

▶Do not contact the terminals while the power is applied. It can cause malfunction.

▶When cleaning or driving a terminal screw, perform them after the power has been turned off.

▶Do not perform works while the power is applied, which can cause disorder or malfunction.

CAUTION

!

▶Do not separate the module from the printed circuit board(PCB), or do not remodel

the module. They can cause disorder, malfunction, damage of the module or a fire.

When mounting or dismounting the module, perform them after the power has been turned off.

▶Do not perform works while the power is applied, which can cause disorder or malfunction.

CAUTION

!

 Waste Disposal Precautions

▶When disposing the module, do it as an industrial waste.

1. Introduction

The G6F-DA2V/G6F-DA2I is digital/analog conversion module for use with the GLOFA PLC GM6 series CPU modules. The D/A conversion module is to convert a 12-bit signed binary digital value to an analog output signal(Voltage or Current).

2. General Specifications

| No | Item | Specifications |  |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ |  |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ |  |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency | Acceleration |  |  | Amplitude |  | Sweep count |  |
|  |  | 10≤f∠57 Hz | - |  |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz | 9.8㎨ {1G} |  |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz | - |  |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz | 4.9㎨{0.5G} |  |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  | LGIS Standard |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient & burst noise | Severity Level | All power modules | Digital I/Os ( Ue  24 V) |  | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage | 2 kV | 1 kV |  | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |  |

G6F-DA2V

V+

V-

CH0

G6F-DA2V

V+

V-

CH1

V+

V-

CH2

V+

V-

CH3

-10~+10V

RUN

①

G6F-DA2I

I+

I-

CH0

G6F-DA2I

I+

I-

CH1

I+

I-

CH2

I+

I-

CH3

4 ~ 20㎃

RUN

3. Performance Specifications

| Items |  | Specifications |  |
| --- | --- | --- | --- |
|  |  | G6F-DA2V | G6F-DA2I |
| Digital input |  | 16bit(data part :12bits)signed binary(-48 ~ 4047) |  |
| Analog output |  | -10 ~ 10VDC (External load resistance : 2kΩ~ 1MΩ) | 4 ∼ 20mADC (External load resistance : less than 510Ω) |
| Max. resolution |  | 5㎷ (1/4000) | 4μA(1/4000) |
| Accuracy |  |  0.5%［Full Scale］ |  |
| Max. conversion speed (ms/channel) |  | 10ms/4 channels |  |
| Max. absolute input |  | 15VDC | 25 mA DC |
| Analog output points |  | 4channels/1module |  |
| Isolation |  | Between input terminals and the PLC: Photo-coupler isolation |  |
| Terminals connected consumption |  | 9-point terminal block |  |
| Internal current consumption | DC+5V | 40mA | 40mA |
|  | DC+15V | 80mA | 120mA |
|  | DC-15V | 60mA | 25mA |
| Weight |  | 200g | 200g |

CAUTION

!

The adjusted value of D/A conversion module at manufacturer has been in the range of

from -10 to 10 VDC or 4 ~ 20mA, and in accordance with it, offset / gain values is fixed .

4. Parts Name and Functions

This following shows the names of parts and functions of G6F-DA2V and G6F-DA2I module.

①

1

2

D/A

Converter

Circuit

CH3

510Ω

7

8

510Ω

GND

CH0

*1

*1

D/A

Converter

Circuit

GND

| No. | Descriptions |  |
| --- | --- | --- |
| ① | RUN LED |  |
|  | Indicates the operating status the G6F-DA2V/G6F-DA2I *Normal mode -On: Normal operation -Off: 5 VDC power off or the G6F-DA2V/G6F-DA2I module fault. |  |

5. Handling Precautions

From unpacking to installation, be sure to check the following:

1) Do not drop it off, and make sure that strong impacts should not be applied.

2) Do not dismount printed circuit boards from the case. It can cause malfunctions.

3) During wiring, be sure to check any foreign matter like wire scraps should not enter into the

upper side of the PLC, and in the event that foreign matter entered into it, always eliminate it.

4) Be sure to disconnect electrical power before mounting or dismounting the module.

6. Wiring

6.1 Wiring Precaution

- Separate AC and output signal of D/A conversion module wiring not to be affected by

surge or induced noise of the AC.

- External wiring has to be at least AWG22(0.3㎟) and be selected in consideration of operating

ambiance and/or allowable current.

- Separate wiring from devices and/or substances generating intense heat, and oil not to make

short-circuit which leads to damage and/or mis-operation.

- Identify the polarity of terminal block before external power supply is made connected.

- Separate external wiring sufficiently from high voltage and power supply cable not to cause

induced failure and/or malfunction.

6.2 Wiring example

1)G6F-DA2V

GND

1

2

D/A

Converter

Circuit

CH3

2㏀~

1㏁

7

8

2㏀~

1㏁

GND

CH0

*1

*1

D/A

Converter

Circuit

2)G6F-DA2I

*1 For the cable, use a two-core twisted shielded wire

7. Dimension

90.0

G6F-DA2I

I+

I-

CH0

G6F-DA2I

I+

I-

CH1

I+

I-

CH2

I+

I-

CH3

4 ~ 20㎃

RUN

35.0

110.0

(Unit : mm)