Data Sheet

LG Programmable Logic Controller

Comuter Link(Cnet) Module

G6L-CUEB

GLOFA-GM

G6L-CUEC

LG Industrial Systems

● Beijing Branch             	● Bangkok Branch

LG Industrial Systems 		LG Industrial Systems (Thailand)

Elevator Co., Ltd. 		Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch          	● Chicago Branch

LG Industrial Systems de 	LG Industrial Systems Co., Ltd.

Colombia S.A.    		Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch              	● Hanoi Branch

Dalian LG Industrial Systems 	LG Industrial Systems Co., Ltd.

Co., Ltd.      		Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch         	● Shanghai Branch

LG Industrial Systems (HK) Ltd.   Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch          	● Taipei Branch

LG Industrial Systems Co., Ltd.    LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

702005650

Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming software) | 702005047 |
| GLOFA GMWIN (Instruction & Programming) | 702005058 |
| GLOFA GM6 (User’s manual) | 702005581 |
| GLOFA GM Cnet (User’s manual) | 702005069 |

| Name | GLOFA-GM G6L-CUEB/CUEC Data Sheet |
| --- | --- |
| Code | 702005650 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the GLOFA G6L-CUEB/CUEC module.

For safety precautions on the PLC system, please see the GLOFA GM6 user’s manual.

If not provided with proper prevention, it can cause death, fatal injury or considerable loss or property

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

WARNING

!

CAUTION

!

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard.

However, a precaution followed with    CAUTION  can also result in serious condition. Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it.

Keep this manual handy for your quick reference in necessary.

 Design Precaution

CAUTION

Do not run I/O signal lines near to high voltage line or power line. Separate them as 100mm or more as possible. Otherwise, noise can cause module malfunction

 Installation Precaution

CAUTION

Operate the PLC in the environment conditions given in the general specifications

If the PLC is operated in other environment not specified in the general specification, it can cause an electric shock, a fire, malfunction or damage or degradation of the module.

Make sure the module fixing projections is inserted into the module fixing hole and fixed.

Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

CAUTION

CAUTION

When grounding a FG terminal, be sure to provide class 3 grounding which is dedicated to the PLC.

Before the PLC wiring, be sure to check the rated voltage and terminal arrangement for the module and observe them correctly.

Drive the terminal screws firmly to the defined torque. If loosely driven, it can cause short circuit, fire or malfunction.

Be careful that any foreign matter like wire scraps should not enter into the module. It can cause a fire, disorder or malfunction.

 Test RUN and Maintenance Precautions

WARNING

Do not contact the terminals while the power is applied. It can cause malfunction.

When cleaning or driving terminal screws, perform them after the power has been turned off.

Do not perform works while the power is applied. It can cause disorder or malfunction.

Do not separate the PCB from the case of module, or do not remodel the module. They can cause disorder, malfunction, damage of the module or a fire.

 Waste Disposal Precautions

CAUTION

When disposing the module, do it as an industrial waste.

1. Introduction

This data sheet contains the brief information about the characteristics, configurations, and operating of GLOFA PLC Computer Link (Cnet) module.

2. General Specifications

| No. | Item | Specification |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency | Acceleration |  | Amplitude |  | Sweep count | IEC 1131-2 |
|  |  | 10≤f∠57 Hz | - |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz | 9.8㎨ {1G} |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz | - |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz | 4.9㎨{0.5G} |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient burst noise | Severity Level | All power modules | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage | 2 kV | 1 kV | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |

3. Performance Specifications

5. 각 부의 명칭과 역할

| Item |  | Specifications |  |  |
| --- | --- | --- | --- | --- |
| Serial Communication Channel |  | RS-232C 1 Channel |  | RS-232C standards conformed. |
|  |  | RS-422/485 1 Channel[1] |  | RS-422/485 standard conformed. |
| MODEM Connection Function |  | Remote communication with external devices such as computer, etc. is possible via public telephone line by connecting external modem to Cnet[2] |  |  |
| Operating Mode |  | Dedicated Protocol | Supporting multidrop/1:1 communication by using dedicated protocol for LG Industrial Systems. |  |
|  |  | GMWIN Protocol | PLC remote control is possible through GMWIN by using its connection function for GLOFA PLC. |  |
|  |  | User-defined Protocol | Operated by user defined protocol using frame editor (for other manufacturer’s interface) |  |
| Data Type | Data Bit | 7 or 8 | With frame editor, basic parameter is able to be selected |  |
|  | Stop Bit | 1 or 2 |  |  |
|  | Start Bit | 1 or 2 |  |  |
|  | Parity | Even / Odd / None |  |  |
| Synchronization Type |  | Asynchronous type |  |  |
| Transmission speed (bps) |  | 300/600/1200/2400/4800/9600/19200/38400 |  |  |
| Station No. Setting |  | Set by using frame editor, Max. 32 stations are able to be set (from 0 to 31) |  |  |
| Transmission Distance |  | RS-232C : Max. 15m(Extendible with MODEM) |  |  |
|  |  | RS-422 : Max. 500m |  |  |
| Diagnosis Function |  | Loop-Back diagnosis |  |  |
|  |  | Indication of operating status with 16 LEDs during operating |  |  |
| Current Consumption |  | 160mA or less |  |  |
| Weight |  | G6L-CUEB : 94g / G6L-CUEC : 102g |  |  |

[1] To use RS-485 channel, select RS-485 mode with frame editor.

[2] To use RS-232C channel via MODEM, select MODEM connection at the setting menu of RS-232C communication type of the frame editor.

4. Cable Specifications

When using RS-422 or RS-485 communication channel, twisted pair cable shall be used with consideration of communication distance and speed. Table 4.1 describes recommended specifications of cable. Also when using another cable than recommended one, the cable conformed to characteristics of Table 4.1 shall be used.

- Item : Low Capacitance Lan Interface Cable

- Type : LIREV-AMESB

- Size : 2P X 22AWG(D/0.254 TA)

- Manufacturer : LG Cable Co., Ltd.

[Table 4.1] Specification of GLOFA Cnet twisted pair cable

| 1) Electrical characteristics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Item |  | Unit | Characteristics |  | Test Condition |  |
| Conductor Resistance |  | /kM | 59 or less |  | General temperature |  |
| Withstanding Voltage (DC) |  | V/1min | 500V, 1 minute |  | In air |  |
| Insulation Resistance |  | MEGA -kM | 1,000 or more |  | General temperature |  |
| Capacity |  | pf/M | 45 or less |  | 1 kHz |  |
| Characteristic Impedance |  |  | 120  12 |  | 10 MHz |  |
| 2) Appearance Characteristics |  |  |  |  |  |  |
| Items |  |  | Solid Cable |  |  | Standard Cable |
| Conductor | Core | Pair | 2 |  |  | 2 |
|  | Size | AWG | 22 |  |  | 22 |
|  | Outer Diameter | mm | 0.64 |  |  | 0.76 |
| Insulator | Thickness | mm | 0.55 |  |  | 0.55 |
|  | Outer Diameter | mm | 1.64 |  |  | 1.76 |

5. Parts Name and Descriptions

6. LED Indication and Operation Mode Switch

[G6L-CUEB]                         [G6L-CUEC]

RUN    NAK

## TX    COM-ERROR

##### RX    MODEM

ACK    SYS-RUN/ERR

G6L-CUEB

RUN    NAK

## TX    COM-ERROR

##### RX    RS-485

ACK    SYS-RUN/ERR

G6L-CUEC

①

①

###### MODE

0:USER DEFINED

1:DEDICATED

2:GMWIN

3:REMOTE

4:TEST

###### MODE

0:USER DEFINED

1:DEDICATED

2:GMWIN

3:REMOTE

4:TEST

②

②

RDA

RDB

③

③

SDA

SDB

RS-232C

SG

FG

RS-422/485

G6L-CUEC

G6L-CUEB

| No. | Name | Descriptions |
| --- | --- | --- |
| ① | LED Indicators | Shows the operation status of G6L-CUEB/G6L-CUEC |
| ② | Mode Switch | Operating mode setting |
| ③ | RS-232C/RS-422/RS-485 Connector | The connector for external connection |

During normal operation, 8 points LED shows the operation and communication status of the module.

1) Operation status (G6L-CUEB)

| LED No. | LED Name | Description | Remarks |
| --- | --- | --- | --- |
| 0 | RUN | On during channel operation |  |
| 1 | TX | On during transmission |  |
| 2 | RX | On during receiving |  |
| 3 | ACK | On during ACK transmission / Off after NAK transmission |  |
| 4 | NAK | On during NAK transmission / Off after ACK transmission |  |
| 5 | COM-ERROR | On when Protocol Error / SIO-Error occurred |  |
| 6 | MODEM | On during modem communication mode is set |  |
| 7 | SYS-RUN/ERR | On when interface error occurred Flickering when serious error occurred | LED 0~4 will show the error status |

2) Operation status (G6L-CUEC)

| LED No. | LED Name | Description | Remarks |
| --- | --- | --- | --- |
| 0 | RUN | On during channel operation |  |
| 1 | TX | On during transmission |  |
| 2 | RX | On during receiving |  |
| 3 | ACK | On during ACK transmission / Off after NAK transmission |  |
| 4 | NAK | On during NAK transmission / Off after ACK transmission |  |
| 5 | COM-ERROR | On when Protocol Error / SIO-Error occurred |  |
| 6 | RS-485 | On : RS-485 mode / Off : RS-422 mode |  |
| 7 | SYS-RUN/ERR | On when interface error occurred Flickering when serious error occurred | LED 0~4 will show the error status |

3) Operation Mode Switch

The operation mode of Cnet module is set with the operation mode switch on the front panel. The change of mode setting switch does not take effect until the Cnet module is reset. (power off and re-applied) Therefore, even the operation mode switch setting is changed during operation, it will take effect after resetting the module. The following table shows switch value and relevant operation mode.

| Switch | Switch Value | Operation Mode | Remarks |
| --- | --- | --- | --- |
|  |  | RS-232C, RS-422 |  |
|  | 0 | User defied |  |
|  | 1 | Dedicated |  |
|  | 2 | GMWIN service |  |
|  | 3 | Not used |  |
|  | 4 | Test mode |  |
|  | 5~8 | Reserved (Not used) |  |
|  | 9 | Download mode |  |

7. Installation and Wiring

### Max. 2 Cnet modules can be mounted on one base board.

### 6.1 RS-232C Interface

RS-232C channel uses 9-pin female connector for communication with external devices.

[Pin assignment of RS-232C 9-pin connector]

| Pin No. | Name | Function | Signal direction (Cnet<-->External device) | Description |
| --- | --- | --- | --- | --- |
| 1 | CD | Carrier Detect |  | DCE inform carrier detection to DTE |
| 2 | RxD | Received Data |  | Received data signal |
| 3 | TxD | Transmitted Data |  | Transmitted data signal |
| 4 | DTR | Data Terminal Ready |  | DTE inform communication ready to DCE |
| 5 | SG | Signal Ground |  | Signal ground line |
| 6 | DSR | Data Set Ready |  | DCE inform communication ready to DTE |
| 7 | RTS | Request To Send |  | DTE require data transmission to DCE |
| 8 | CTS | Clear To Send |  | DCE inform ready to transmit to DTE |
| 9 | RI | Ring |  | DCE inform receiving ‘Ringing Tone’ to DTE |

When connection modem, communication type of RS-232C must be set to ‘modem’ with frame editor, and when not using modem, it must be set to null modem. But when the channel mode is an interlocking one, modem cannot be connected because it is operated as null modem even though setting to modem.

* DTE:Data Terminal Equipment

* DCE:Data Communication Equipment

- 1) How to connect RS-232C connector during modem connection

- Cnet can communicate with devices of long distance with modem connected, at this time modem and channel RS-232C must be connected as shown in below table.

| Cnet(9-PIN) |  | Connection No. and Signal Direction | Modem (25-PIN) |  |
| --- | --- | --- | --- | --- |
| Pin No. | Name |  | Name | Pin No. |
| 1 | CD |  | CD | 8 |
| 2 | RXD |  | RXD | 3 |
| 3 | TXD |  | TXD | 2 |
| 4 | DTR |  | DTR | 20 |
| 5 | SG |  | SG | 7 |
| 6 | DSR |  | DSR | 6 |
| 7 | RTS |  | RTS | 4 |
| 8 | CTS |  | CTS | 5 |
| 9 | RI |  | RI | 22 |

2) How to connect RS-232C connector in null modem mode

In null modem mode, connector is able to be connected in 7-line (with handshake) or 3-line (without handshake) type.

[ 7-line connection (with handshake)]

| Cnet(9-PIN) |  | Connection No. and Signal Direction | Computer/Communication device |
| --- | --- | --- | --- |
| Pin No. | Name |  | Name |
| 1 | CD |  | CD |
| 2 | RXD |  | RXD |
| 3 | TXD |  | TXD |
| 4 | DTR |  | DTR |
| 5 | SG |  | SG |
| 6 | DSR |  | DSR |
| 7 | RTS |  | RTS |
| 8 | CTS |  | CTS |
| 9 | RI |  | RI |

If CD signal line is not controlled from external devices, it must be connected in 3-line type as shown in below table. Recent PC does not handle CD signal line, so when connecting with PC, it must be connected in 3-line type.

[ 3-line connection (without handshake)]

| Cnet(9-PIN) |  | Connection No. and Signal Direction Name | Computer/Communication device |
| --- | --- | --- | --- |
| Pin No. | Name |  | Name |
| 1 | CD |  | CD |
| 2 | RXD |  | RXD |
| 3 | TXD |  | TXD |
| 4 | DTR |  | DTR |
| 5 | SG |  | SG |
| 6 | DSR |  | DSR |
| 7 | RTS |  | RTS |
| 8 | CTS |  | CTS |
| 9 | RI |  | RI |

6.2 RS-422 Interface

Rs-422 channel uses 6-pin connector (terminal block) for communication with external devices. The names and functions of pins, and data directions are as shown in the following table.

[ Pin assignment of RS-422 6-pin connector]

| Pin No. | Name | Signal direction (Cnet<-->External device) | Function |
| --- | --- | --- | --- |
| 1 | RDA |  | Received data (+) |
| 2 | RDB |  | Received data (-) |
| 3 | SDA |  | Transmitted data (+) |
| 4 | SDB |  | Transmitted data (-) |
| 5 | S.G |  | Signal ground line |
| 6 | F.G |  | Frame ground line |

RS-422 channel makes connection external devices and RS-422 and RS-485(Multidrop) possible. When RS-422 channel is used as multidrop, set channel RS-422 to RS-485 communication in setting menu of RS-422 communication type of frame editor, and connect the terminal of RS-422 as shown in the [RS-485 connection] table.

[ RS-422 connection]

| Computer link |  | Signal direction (Cnet<--->External device) | External device |
| --- | --- | --- | --- |
| Pin No. | Name |  |  |
| 1 | RDA |  | SDA |
| 2 | RDB |  | SDB |
| 3 | SDA |  | RDA |
| 4 | SDB |  | RDB |
| 5 | S.G |  | S.G |
| 6 | F.G |  | F.G |

[ RS-485 connection]

| Computer link |  | Signal direction (Cnet<--->External device) | External device |
| --- | --- | --- | --- |
| Pin No. | Name |  |  |
| 1 | RDA |  | RDA |
| 2 | RDB |  | RDB |
| 3 | SDA |  | SDA |
| 4 | SDB |  | SDB |
| 5 | S.G |  | S.G |
| 6 | F.G |  | F.G |

Above figure show how to connect RS-485 multidrop communication. In the case of multidrop communication, to connect with external devices RDA and SDA, RDB and SDB of channel RS-422 should be connected each other. At this time, half-duplex communication in run sharing Tx/Rx line, so channel RS-422 mode should be set to RS-485 in frame editor.

8. Terminal Resistance (RS-422/RS-485)

When the communication via channel RS-422, terminal resistor from external must be connected. Terminal resistor has the function to prevent distortion of signal by reflected wave of cable when long distance communication, the same resistor (1/2W) as characteristic impedance of cable must be connected to terminal of network.

When using the recommended cable in the chapter 4, connect terminal resistor of 120 to both ends of cable. Also when using another cable than recommended one, the same resistor (1/2W) as characteristic impedance of cable must be connected to both ends of cable.

1) How to connect terminal resistor [RS-422 connection]

2) How to connect terminal resistor [RS-485 connection]

9. Handling Instructions

1) All the station in whole network should not have duplicated station number. Otherwise, it can cause serious communication error.

2) Use cable complying with specification in this data sheet. Otherwise, it can cause a serious communication error.

3) Make sure that communication cable does not break or short.

4) Make sure that cable connector is fastened with recommended torque. Loose connection could cause serious communication error.

5) Improper cable connection(snarled cable, redundant connection) can cause communication error.

6) While the power of module is on, mounting/dismounting of module will cause system error and the CPU module halted. Therefore, turn the power off during replacing or repairing module.

7) If the station number of operation mode is changed while power is on, the module should be reset (turn power off and turn on again) to take effect those changes.

10. Dimensions

G6L-CUEB and G6L-CUEC have the same dimensions.

Unit : mm

110

35

81.1

90