Data Sheet

LG Programmable Logic Controller

High Speed Counter Module

GLOFA-GM

G6F-HSCA

LG Industrial Systems

● Beijing Branch             	● Bangkok Branch

LG Industrial Systems 		LG Industrial Systems (Thailand)

Elevator Co., Ltd. 		Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch          	● Chicago Branch

LG Industrial Systems de 	LG Industrial Systems Co., Ltd.

Colombia S.A.    		Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch              	● Hanoi Branch

Dalian LG Industrial Systems 	LG Industrial Systems Co., Ltd.

Co., Ltd.      		Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch         	● Shanghai Branch

LG Industrial Systems (HK) Ltd.   Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch          	● Taipei Branch

LG Industrial Systems Co., Ltd.    LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

702005650

Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming software) | 702005047 |
| GLOFA GMWIN (Instruction & Programming) | 702005058 |
| GLOFA GM6 (User’s manual) | 702005581 |
| GLOFA GM6 High Speed Counter (User’s manual) | 702005069 |

| Name | GLOFA-GM G6L-CUEB/CUEC Data Sheet |
| --- | --- |
| Code | 702005650 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the GLOFA G6L-CUEB/CUEC module.

For safety precautions on the PLC system, please see the GLOFA GM6 user’s manual.

If not provided with proper prevention, it can cause death, fatal injury or considerable loss or property

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

WARNING

!

CAUTION

!

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard.

However, a precaution followed with    CAUTION  can also result in serious condition. Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it.

Keep this manual handy for your quick reference in necessary.

 Design Precaution

CAUTION

Do not run I/O signal lines near to high voltage line or power line. Separate them as 100mm or more as possible. Otherwise, noise can cause module malfunction

 Installation Precaution

CAUTION

Operate the PLC in the environment conditions given in the general specifications

If the PLC is operated in other environment not specified in the general specification, it can cause an electric shock, a fire, malfunction or damage or degradation of the module.

Make sure the module fixing projections is inserted into the module fixing hole and fixed.

Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

CAUTION

CAUTION

When grounding a FG terminal, be sure to provide class 3 grounding which is dedicated to the PLC.

Before the PLC wiring, be sure to check the rated voltage and terminal arrangement for the module and observe them correctly.

Drive the terminal screws firmly to the defined torque. If loosely driven, it can cause short circuit, fire or malfunction.

Be careful that any foreign matter like wire scraps should not enter into the module. It can cause a fire, disorder or malfunction.

 Test RUN and Maintenance Precautions

WARNING

Do not contact the terminals while the power is applied. It can cause malfunction.

When cleaning or driving terminal screws, perform them after the power has been turned off.

Do not perform works while the power is applied. It can cause disorder or malfunction.

Do not separate the PCB from the case of module, or do not remodel the module. They can cause disorder, malfunction, damage of the module or a fire.

 Waste Disposal Precautions

CAUTION

When disposing the module, do it as an industrial waste.

1. Introduction

This data sheet contains the brief information about the characteristics, configurations, and operating of GM6 high speed counter module.

2. General Specifications

| No. | Item | Specification |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency | Acceleration |  | Amplitude |  | Sweep count | IEC 1131-2 |
|  |  | 10≤f∠57 Hz | - |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz | 9.8㎨ {1G} |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz | - |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz | 4.9㎨{0.5G} |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient burst noise | Severity Level | All power modules | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage | 2 kV | 1 kV | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |

3. Performance Specifications

5. 각 부의 명칭과 역할

| Item | Specifications |  |  |
| --- | --- | --- | --- |
| Number of Channels | 1 channel |  |  |
| Counter input signal | Signal | Phase A, Phase B or Phase Z |  |
|  | Signal level | 5 / 12 / 24 VDC (7mA) |  |
|  | Signal type | Voltage input |  |
| Counting range | 0 to 16,777,215 (24 Bits Binary) |  |  |
| Counting speed | Maximum 50 kHz |  |  |
| Preset Operation | Set by connector signal or program |  |  |
| Limit switch input | 24 VDC |  |  |
| Setting Increment /Decrement | 1-phase input |  | Set by program or Phase B is set |
|  | 2-phase input |  | Set by difference of phase automatically |
| External output | Type |  | Out 1, Out 2(One among ‘>’, ‘=’ and ‘<’ is selected) |
|  | Signal type |  | Transistor output ( open collector output, 10 to 30 V) |
| Multiplication | The multiplication factor for the input pulse may be set to 1, 2 or 4 (Selected by DIP Switch adjustment) |  |  |
| Current consumption | 5 VDC, 180 mA |  |  |
| Weight | 160 g |  |  |

4. I /O Specifications

1) Input Specifications

| Item | Specifications |  |
| --- | --- | --- |
| Rated input voltage / current | 5 VDC (7 mA) |  |
|  | 12 VDC (7 mA) |  |
|  | 24 VDC (7 mA) |  |
| ' On ' guarantee voltage | 5 VDC | 4.5 V or more |
|  | 12 VDC | 11 V or more |
|  | 24 VDC | 14 V or more |
| ' Off ' guarantee voltage | 5 VDC | 0.8 V or less |
|  | 12 VDC | 1.5 V or less |
|  | 24 VDC | 2.5 V or less |

2) Limit Switch(L/S) and Preset(PSET) Input Specifications

| Item | Specifications |
| --- | --- |
| Input voltage | 24 VDC |
| ' On ' guarantee voltage | 19 VDC or more |
| ' Off ' guarantee voltage | 6 VDC or less |
| On Delay Time | 1.5 ms or less |
| Off Delay Time | 2 ms or less |

3) Transistor Output Specifications

| Item | Specifications |
| --- | --- |
| Rated output | 24 VDC, 200 mA |
| Leakage current | 50 μA or less |
| Saturated voltage | 1.3V |
| On Delay Time | 50 μs or less |
| Off Delay Time | 50 μs or less |

5. Parts Name and Descriptions

G6F-HSCA

RDY            L/S

ΦA             PRE

ΦB             PRE

ΦC             PRE

###### Description

Ready (RDY) Turns on when the power is applied

Phase A Input (ΦA) Turns on when voltage is applied to phase A input terminal.

Phase B Input (ΦB) Turns on when voltage is applied to phase B input terminal

Phase Z Input (ΦZ) Turns on when voltage is applied to phase B input terminal

Limit Switch Input (L/S) Turns on when voltage is applied to limit switch input terminal

Preset Switch Input (PRE) Turns on when voltage is applied to preset switch input terminal

Output 1 (OUT1) Indicate the magnitude comparison result of CMP 1

Output 2 (OUT2) Indicate the magnitude comparison result of CMP 2

2) DIP Switch Setting Part

The DIP Switch settings are used for phase-2/ phase-1 operation mode specification, Increment / Decrement count method specification at 1-phase operation, and multiplication specification at 2-phase operation.

| Switch | #### Functions |  |
| --- | --- | --- |
|  | Status | Descriptions |
| SW 1 | ON | Specifies the 2 – phase pulse operation mode. |
|  | OFF | Specifies the 1 – phase pulse operation mode. |
| SW 2 | ON | Specifies the phase B pulse input mode as increment/decrement count method at 1 phase pulse inputs |
|  | OFF | Specifies the program input mode as increment/decrement count method at 1 phase pulse inputs |
| SW 3 SW 4 | ON ON | Specifies multiplication 1 |
|  | ON OFF | Specifies multiplication 2 |
|  | OFF ON | No multiplication is applied |
|  | OFF OFF | Specifies multiplication 4 |

3) I/O terminal connector

6. Installation and Test Run

8. Dimension (mm)

6.1  Ambiance Requirements

Avoid installing this module in locations, which are subjected or exposed to:

▶ Water leakage and dust a large amount of dust, powder and other conductive power, oil mist, salt, of organic solvent

▶ Mechanical vibrations of impacts transmitted directly to the module body.

▶ Direct sunlight.

▶ Dew condensation due to sudden temperature change.

▶ High or low temperatures (outside the range of 0-55℃)

6.2  Installing and Wiring

▶ During wiring or other work, do not allow any wire scraps to enter into it.

▶ Install it on locations that are convenient for operation.

▶ Make sure that it is not located near high voltage equipment on the same panel.

▶ Make sure the distance from the walls of duct and external equipment be 50 mm or more.

▶ Be sure to be grounded to locations that have good noise immunity.

6.3  Test Run

| ## REMARK |  |
| --- | --- |
| Please check the voltage level of input terminal is proper before the power is applied to the encoder. For example, if 24 V is given for 5 V input, it can cause faults. |  |

● Check Items before the Power Is Applied.

1. Check if the input signal is 1-phase, or 2-phase.

2. Check if the adjustment of DIP switch according to input signal type.

3. Check the wiring on terminal block is correct.

4. Check if the external power is correct.

7. Wiring

| I/O | Internal Current | Terminal pin No. | Signal Name | Operation | Input guarantied Voltage |
| --- | --- | --- | --- | --- | --- |
| Input |  | 1 | 24 V, Phase A pulse input | ON | 14~26.4 V |
|  |  |  |  | OFF | 2.5 V |
|  |  | 2 | 12 V, Phase A pulse input | ON | 11~13.2 V |
|  |  |  |  | OFF | 1.5 V |
|  |  | 3 | 5 V, Phase A pulse input | ON | 4.5~5.5 V |
|  |  |  |  | OFF | 0.8 V or less |
|  |  | 4 | COM |  |  |
|  |  | 5 | 24 V, Phase B pulse input | ON | 14~26.4 V |
|  |  |  |  | OFF | 2.5 V |
|  |  | 6 | 12 V, Phase B pulse input | ON | 11~13.2 V |
|  |  |  |  | OFF | 1.5 V |
|  |  | 7 | 5 V, Phase B pulse input | ON | 4.5~5.5 V |
|  |  |  |  | OFF | 0.8 V or less |
|  |  | 8 | COM |  |  |
|  |  | 9 | 24 V, Phase Z pulse input | ON | 14~26.4 V |
|  |  |  |  | OFF | 2.5 V |
|  |  | 10 | 12 V, Phase Z pulse input | ON | 11~13.2 V |
|  |  |  |  | OFF | 1.5 V |
|  |  | 11 | 5 V, Phase Z pulse input | ON | 4.5~5.5 V |
|  |  |  |  | OFF | 0.8 V or less |
|  |  | 12 | COM |  |  |
| Input |  | 13 | L/S input 24 V | ON | 19~26.4 V |
|  |  |  |  | OFF | 6 V or less |
|  |  | 14 | L/S COM |  |  |
|  |  | 15 | Preset input 24V | ON | 19~26.4 V |
|  |  |  |  | OFF | 6 V or less |
|  |  | 16 | L/S COM |  |  |
| Output |  | 17 | Open collector output OUT1 | Rated output: 24VDC, 200 mA Response time: OFF ON50μs or less ONOFF 50μs or less |  |
|  |  | 18 | Open collector output OUT2 |  |  |
|  |  | 37 | External power supply output 24 V | Input voltage 10.2 ~ 30 V |  |
|  |  | 19 | External power supply COM 0 V |  |  |

[ An example of wiring : DC5V, Voltage output]

Shielded cable

Shielded cable

Shielded cable

External Power

Pulse Generator

Limit Switch

L/S input +24V

External power +24V

Relay

Relay

External power

270Ω

270Ω

820Ω

820Ω

820Ω

Preset input

Preset input +24V

Preset COM

[The output mode of encoder]

G6F-HSCA

3.3kΩ

G6F-HSCA

3.3kΩ

Open collector output

Voltage output