Data Sheet

LG Programmable Logic Controller

FieldBus Network Option Module

G0L-FREA

G0L-FOEA

G0L-FACA

G0L-FABA

G0L-FAPA

GLOFA-GM

LG Industrial Systems

● Beijing Branch             	● Bangkok Branch

LG Industrial Systems 		LG Industrial Systems (Thailand)

Elevator Co., Ltd. 		Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch          	● Chicago Branch

LG Industrial Systems de 	LG Industrial Systems Co., Ltd.

Colombia S.A.    		Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch              	● Hanoi Branch

Dalian LG Industrial Systems 	LG Industrial Systems Co., Ltd.

Co., Ltd.      		Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch         	● Shanghai Branch

LG Industrial Systems (HK) Ltd.   Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch          	● Taipei Branch

LG Industrial Systems Co., Ltd.    LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

702005627

Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming software) | 702005047 |
| GLOFA GM (Instruction & Programming) | 702005058 |
| GLOFA GM3/4 (User’s Manual) | 702005581 |
| GLOFA GM6 (User’s manual) | 702005581 |
| GLOFA GM Fnet/Mnet (User’s manual) | 702005070 |

| Name | GLOFA-GM Fnet Option Data Sheet |
| --- | --- |
| Code | 702005627 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the GLOFA Fnet option modules.

For safety precautions on the PLC system, please see the GLOFA GM Fnet user’s manual.

If not provided with proper prevention, it can cause death, fatal injury or considerable loss or property

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

WARNING

!

CAUTION

!

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard.

However, a precaution followed with    CAUTION  can also result in serious condition. Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it.

Keep this manual handy for your quick reference in necessary.

 Design Precaution

CAUTION

Do not run I/O signal lines near to high voltage line or power line. Separate them as 100mm or more as possible. Otherwise, noise can cause module malfunction

 Installation Precaution

CAUTION

Operate the PLC in the environment conditions given in the general specifications

If the PLC is operated in other environment not specified in the general specification, it can cause an electric shock, a fire, malfunction or damage or degradation of the module.

Make sure the module fixing projections is inserted into the module fixing hole and fixed.

Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

CAUTION

CAUTION

When grounding a FG terminal, be sure to provide class 3 grounding which is dedicated to the PLC.

Before the PLC wiring, be sure to check the rated voltage and terminal arrangement for the module and observe them correctly.

Drive the terminal screws firmly to the defined torque. If loosely driven, it can cause short circuit, fire or malfunction.

Be careful that any foreign matter like wire scraps should not enter into the module. It can cause a fire, disorder or malfunction.

 Test RUN and Maintenance Precautions

WARNING

Do not contact the terminals while the power is applied. It can cause malfunction.

When cleaning or driving terminal screws, perform them after the power has been turned off.

Do not perform works while the power is applied. It can cause disorder or malfunction.

Do not separate the PCB from the case of module, or do not remodel the module. They can cause disorder, malfunction, damage of the module or a fire.

 Waste Disposal Precautions

CAUTION

When disposing the module, do it as an industrial waste.

1. Introduction

This data sheet contains the brief information about the characteristics, configurations, and operating of GLOFA PLC Fnet option modules.

2. General Specifications

| No. | ###### Item | Specification |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency | Acceleration |  | Amplitude |  | Sweep count | IEC 1131-2 |
|  |  | 10≤f∠57 Hz | - |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz | 9.8㎨ {1G} |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz | - |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz | 4.9㎨{0.5G} |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient burst noise | Severity Level | All power modules | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage | 2 kV | 1 kV | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |

3. Performance Specifications

| Model Item |  | G0L-FREA | G0L-FOEA | G0L-FACA | G0L-FABA | G0L-FAPA |
| --- | --- | --- | --- | --- | --- | --- |
| Transfer rate |  | 1Mbps |  |  |  |  |
| Comm. Method |  | Half duplex bit serial method |  |  |  |  |
| Synchronization |  | Frame synchronous method |  |  |  |  |
| Transmission method |  | Bus type |  |  |  |  |
| Max. cable length |  | 750m | 750m/3km | 3km |  |  |
| Modulation |  | Manchester Biphase-L |  |  |  |  |
| Error detect |  | CRC-CCITT and Time Over |  |  |  |  |
| RAS function |  | ㆍTransmission error detection ㆍReceived waveform error detection |  |  |  |  |
| Connector type |  | Electrical : 9-pin plug type Optical : Tx/Rx connector |  |  |  |  |
| Power Supply |  | AC110V ~ 220V, DC24V |  |  |  |  |
| Cable type |  | Electrical : Twisted pair cable Optical : Optical fiber cable |  |  |  |  |
|  |  | Electrical | Electrical/optical | Optical |  |  |
| Current consumption | AC110V | 24mA | 26mA |  |  | 26mA |
|  | DC24V | 102mA | 128mA |  |  | 121mA |
| Weight |  | 430g | 432g | 66g | 1242g | 252g |

4. Cable Specifications

 Twisted pair cable

| Type | LIREV-AMESB 2*1.0mm 18AWG | Structure |
| --- | --- | --- |
| Manufacturer | LG Cable | Conductor Insulator Shield Ground line |
| Cable Type | Twisted pair shielded cable |  |
| Impedance | 21.8Ω/㎞ |  |
| Withstanding Voltage(DC) | 500 V/min |  |
| Insulation resistance | 1,000㏁/㎞ or more |  |
| Capacity | 45 ㎊/m or less (1㏀) |  |
| Characteristic impedance | 120±12Ω(10㎒) |  |
| Numbers of core | 2 Cores |  |

 Optical cable

| Manufacturer | LG Cable / Hewlett Packard |  | Structure |
| --- | --- | --- | --- |
| Fiber Size (unit : ㎛) | Core | Cladding | Optical fiber Insulator |
|  | 62.5 | 125 |  |
| Connector type | S.T |  |  |
| Cable type | Bi-drectional |  |  |
| Attenuation | 5 dB/km (Max.) |  |  |
|  | 4.5 dB/km (Standard) |  |  |
| N.A (Numerical Attenuation) | 0.275 |  |  |

5. Parts Name and Description

① G0L-FREA

PWR

TRX

INPUT

AC

DC

AC110~220V  FG   24V  24G

G0L-FREA

| Connector | Connectors for FieldBus communication cable (Electrical) |
| --- | --- |
| LED | Indicates the status of communication |
| PWR | Turn on when power is applied |
| TRX A, B | Flickering while normal communication |
| Terminal Block | Connect external power supply (See 7.2 for more details) |
| AC110 ~ 220V | Free voltage |
| FG | Frame ground terminal |
| 24V | +24VDC |
| 24G | -24VDC |

② G0L-FOEA

| Connector | Connectors for FieldBus communication cable (Electrical / optical)) |
| --- | --- |
| ELECTRIC | Electrical cable connector |
| TX | Optical transmission cable connector |
| RX | Optical receiving cable connector |
| LED | Indicates the status of communication |
| PWR | Turn on when power is applied |
| TRX A, B | Flickering while normal communication |
| Terminal Block | Connect external power supply (See 7.2 for more details) |
| AC110 ~ 220V | Free voltage |
| FG | Frame ground terminal |
| 24V | +24VDC |
| 24G | -24VDC |

INPUT

AC

DC

AC110~220V  FG   24V  24G

TX   RX

TX   RX

ELECTRIC

OPTIC-A

OPTIC-B

PWR

TRX

G0L-FOEA

③ G0L-FACA / G0L-FAPA / G0L-FABA

ACTIVE COUPLER

TRX

OPTIC

OPTIC

OPTIC

OPTIC

OPTIC

OPTIC

PWR

AC110-220V

INPUT

NC

FG

RX

RX

TX

RX

TX

RX

TX

RX

TX

RX

DC24V

INPUT

TX

TX

G0L-FABA

G0L-FAPA

G0L-FACA

G0L-FADA

| Connector | Connectors for optical fiber cable |
| --- | --- |
| TX | Optical transmission cable connector |
| RX | Optical receiving cable connector |
| LED | Indicates the status of communication |
| PWR | Turn on when power is applied |
| TRX A, B | Flickering while normal communication |
| Terminal Block | Connect external power supply (See 7.2 for more details) |
| AC110 ~ 220V | Free voltage |
| NC | No connection |
| FG | Frame ground terminal |
| 24V | +24VDC |
| 24G | -24VDC |

6. Fnet System Configuration

GM1 multi-CPU, GM2 system

GM3 remote base

GM4 remote base

GM6 system

GMR Redundancy system

GM3 system

G0L-FUEA

# Active coupler (G0L-FACA)

Repeater(G0L-FREA)  Optical/electric converter(G0L-FOEA)

GM3 remote expansion base

GM4 remote expansion base

: Electrical (twisted pair) cable            : Optical fiber cable

7. Wiring and Installation

  - Assembling an active coupler

The active coupler consist of a base(G0L-FABA), power supply (G0L-FAPA), coupler module (G0L-FACA), and dummy module (G0L-FADA). First, insert a G0L-FAPA into the left slot of G0L-FABA. Then, insert G0L-FACA as many as you want to use. Attach the dummy module (G0L-FADA) at the unused slot to protect from dust or foreign matter. After inserting each module into slot, fasten screws with driver as following picture.

  - The wiring of power supply terminal

The fieldbus option modules G0L-FREA (repeater), G0L-FOEA (optical-electric converter), and G0L-FAPA (power supply module) have dual power supply terminal, Therefore, if a power supply stop operation, the another power supply can operate system without stopping.

AC110 ~ 220V

FG           24V          24G

DC

AC110 ~

220V

(Free Voltage)

~

+

DC24V

_

8. Maintenance

Perform routine check and regular check to maintain the best status of the FieldBus option module.

① Daily Check

| Items to be checked |  | Contents | Criteria of decision | Action to take |
| --- | --- | --- | --- | --- |
| Cable connection status |  | Release of cable | Shall not be any release | Tighten the cable |
| Module connection status |  | Release of screw | Shall not be any release | Tighten the screw |
| G0L-FREA | PWR LED | LED status | LED is on (Off means an error) | Check the power cable |
|  | TRX A LED | LED status | LED is on. (Off means duplicated station or wrong cable connection) | Check the cable. |
|  | TRX B LED |  |  |  |
| G0L-FOEA | PWR LED | LED status | LED is on (Off means an error) | Check the power cable |
|  | TRX LED | LED status | LED is on. (Off means duplicated station or wrong cable connection) | Check the cable. |
| G0L-FAPA | PWR LED | LED status | LED is on (Off means an error) | Check the power cable |
|  | TRX LED | LED status | LED is on. (Off means duplicated station or wrong cable connection) | Check the cable. |

② Regular Check

| Items to be checked |  | How to check | Criteria of decision | Action to take |
| --- | --- | --- | --- | --- |
| Ambient conditions | Ambient temp. | Measure thermometer/hygrometer | 0-55℃ | Adjust it in order to fit to general specifications (for use in panel, inside panel ambient criteria) |
|  | Ambient moisture |  | 5-95% RH |  |
|  | Ambient pollution | Measure corrosive gas | Corrosive gas shall not be there. |  |
| Module state | Loosening, Shaking | Move communication module | It shall be tightly mount-ed. | Tighten screw |
|  | Dust, Foreign matters | Visual inspection | No dust or foreign matters shall be there. |  |
| Connection state | Terminal screw loosened | Tighten with driver | No loosening shall be there. | Tighten |
|  | Closeness of compressed terminal | Visual inspection | Distance shall be suit-able. | Correct |
|  | Connector loosening | Visual inspection | No loosening shall be there. | Tighten connector lock-ing screw. |
| Power voltage check |  | Measure voltage between AC 110/220V terminals | AC 85-264V | Modify power supply. Modify transformer tap. |
|  |  | Measure voltage between DC24V +/- terminals | DC 20 ~ 30V |  |

9. Dimensions

① G0L-FREA, G0L-FOEA

G0L-FOEA and G0L-FREA have same dimension.

(Unit : mm)

142

4

100

88.5

44.3

150

35

② Active Coupler

The following picture shows that G0L-FABA, G0L-FAPA, G0L-FACA is assembled.                                     (Unit : mm)

236

250

 4.3

 8

135

150

88

68.5