## COVER
Training Guide
GLOFA-GM series
GLOFA-GM7
LG INDUSTRIAL SYSTEMS CO,. LTD

## Contents
Contents
| 1. Characteristics | 1
| 2. Functional Specifications | 1
| 3. Configuration | 2
| 4. Analog Input/Output Unit(G7F-ADHA) | 4
| 5. Analog Input Unit(G7F-AD2A) | 6
| 6. Analog Timer(G7F-AT2A) | 8
| 7. Built-in High Speed Counter | 9
| 8. Built-in Pulse output Function | 11
| 9. Pulse Catch Inputs | 14
| 10. Input Filters | 15
| 11. Real time clock | 16
| 12. Option Units | 17

## FEATURES (GM7)
1. Characteristics(GM7)
1. Max. I/O points: 10S(30points), 20S (40points), 30S(50points),
40S (60points), 60S(80points)
2. The user program is stored in a RAM with a battery
or in a Flash memory without a battery.(Program capacity : 68KByte)
External Memory module is prepared for program back-up.
3. Execution speed : 0.5㎲/step
4. Built-in Functions
1) One(1) channel of RS-232C I/F via loader port is available.
Base unit has one RS485 communcation channel.(only for G7M-xx10S)
- Dedicated protocol, User defined protocol, Modbus protocol supported
2) Pulse output 1ch. : 2kpps 1ch. (available for Transistor output)
3) Pulse catch 8points : Min. pulse width 0.2ms
4) Input filter : Applicable to all inputs (0 ~ 15ms)
5) PID 8loops with Autotuning
6) Interrupt input 8ponts
7) One(1) channel of High speed counter(HSC) : 1 Φ(16kpps) or 2 Φ(8kpps)
5. Optional functions
1) The real time clock function is provided(optional),
and it makes scheduled control available.
2) Analog module : I/O = 2ch/1ch, I = 4ch.
3) Analog Timer module : 4ch.
4) Serial I/F module : RS-232C 1ch, RS-422/485 1ch.
2. Functional Specifications(GM7)
| Item | G7M-xx10S | G7M-xx20S | G7M-xx30S | G7M-xx40S | G7M-xx60S
| Program control method | Cyclic and interrupt execution of stored program
| I/O processing method | Refreshing after each scan and direct access
| Programming Language | IL(Instruction List), LD(Ladder Diagram)
| No. of instructions | 30 Basic instruction & 218 application instructions
| Execution time | 0.5㎲/step
| Program capacity | 68KBytes
| Memory device type | RAM or built-in Flash memory
| Max.No.of I/O points(I/O) | 30(18/12) | 40(24/16) | 50(30/20) | 60(36/24) | 80(48/32)
| Direct Variables | 2 ~ 8KBytes
| Symbolic Variables | 32KBytes - Direct Variables
| No. of Timer | No limit within the memory(0.0 ~ 4297967.295sec)
| No. of Counter | No limit within the memory(-32768 ~ 32768)
| No. of Cyclic Programs | 100 programs
| Time Driven Task | 8 programs
| Event Driven Task | 8 programs |  | Total 8 programs
| Internal Flag Driven Task | 8 programs
| Initial Task | 1 program
1

## CONFIG (GM7)
3. Configuration(GM7)
| 1. G7M-DR10S/DT10S |  |  | G7E-DR10A/DT10A
|  | %I0.0.0 ~ 5 |  |  | %I0.x.0 ~ 5 |  |  | %I0.x.0 ~ 5
|  | Input Term. |  |  | Input Term. |  |  | Input Term.
|  | G7M-xx10S |  |  | K7E-DR10S |  |  | K7E-DR10S
|  | Output Term. |  |  | Output Term. |  |  | Output Term.
|  | %Q0.0.0 ~ 3 |  |  | %Q0.x.0 ~ 3 |  |  | %Q0.x.0 ~ 3
|  |  |  | [1st Exp. Unit] |  |  | [2nd Exp. Unit]
2. G7M-DR20S
%I0.0.0 ~ 11
|  | Input Term. | Slot No. 0 1 2 3
|  |  |  | Basic |  | Exp. |  | Exp. |  | Exp.
G7M-xx20S
Back-up memory module
|  | Output Term. | [6 empty] | Real time clock module
%Q0.0.0 ~ 7
3. G7M-DR30S
%I0.0.0 ~ 17
Input Term.
G7M-xx30S
Output Term.
%Q0.0.0 ~ 11
4. G7M-DR40S
%I0.0.0 ~ 23
Input Term.
G7M-xx40S
Output Term.
%Q0.0.0 ~ 15
5. G7M-DR60S
%I0.0.0 ~ 35
Input Term.
G7M-xx60S
Output Term.
%Q0.0.0 ~ 23
2

## TERM. (GM7)
Terminal addressing
| G7M-DR10S / DT10S | [24 empty] | G7E-DR10A / DT10A
Input | I00 |  | I02 |  | I04 |  | COM |  | 485+ |  | 485- | [11 empty] | Input |  |  | I00 |  | I01 |  | I02 |  | I03 |  | I04 |  | I05 |  | COM
|  | I01 |  | I03 |  | I05 |  |  |  | 24G |  | 24V
Output | AC100-240 |  |  |  | Q00 |  | Q01 |  | Q02 |  | Q03
|  | FG |  | COM0 |  | COM1 |  | COM2 |  | COM3 | [12 empty] | Output |  |  | COM0 |  | Q00 |  | COM1 |  | Q01 |  | COM2 |  | Q02 |  | Q03
G7M-DR20S
Input | I00 |  | I02 |  | I04 |  | I06 |  | I08 |  | I10 |  |  | COM0
|  | I01 |  | I03 |  | I05 |  | I07 |  | I09 |  | I11 |  | 24G |  | 24V
Output | AC100-240 |  |  |  | Q00 |  | Q01 |  | Q02 |  | - |  | Q04 |  | Q06
|  | FG |  | COM0 |  | COM1 |  | COM2 |  | Q03 |  | COM3 |  | Q05 |  | Q07
G7M-DR30S
Input | I00 |  | I02 |  | I04 |  | I06 |  | I08 |  | I10 |  | I12 |  | I14 |  | I16 |  |  | COM0
|  | I01 |  | I03 |  | I05 |  | I07 |  | I09 |  | I11 |  | I13 |  | I15 |  | I17 |  | 24G |  | 24V
Output | AC100-240 |  |  |  | Q00 |  | Q01 |  | Q02 |  | - |  | Q04 |  | Q06 |  | - |  | Q08 |  | Q10
|  | FG |  | COM0 |  | COM1 |  | COM2 |  | Q03 |  | COM3 |  | Q05 |  | Q07 |  | COM4 |  | Q09 |  | Q11
K7M-DR40S
Input | I00 |  | I02 |  | I04 |  | I06 |  | I08 |  | I10 |  | COM0 |  | I13 |  | I15 |  | I17 |  | I19 |  | I21 |  | I23 |  | COM1
|  | I01 |  | I03 |  | I05 |  | I07 |  | I09 |  | I11 |  | I12 |  | I14 |  | I16 |  | I18 |  | I20 |  | I22 |  | 24G |  | 24V
Output | AC100-240 |  |  |  | Q00 |  | Q01 |  | Q02 |  | - |  | Q04 |  | Q06 |  | - |  | Q08 |  | Q10 |  | - |  | Q12 |  | Q14
|  | FG |  | COM0 |  | COM1 |  | COM2 |  | Q03 |  | COM3 |  | Q05 |  | Q07 |  | COM4 |  | Q09 |  | Q11 |  | COM5 |  | Q13 |  | Q15
K7M-DR60S
Input | I00 |  | I02 |  | I04 |  | I06 |  | I08 |  | I10 |  | I12 |  | I14 |  | I16 |  | COM0 |  | I19 |  | I21 |  | I23 |  | I25 |  | I27 |  | I29 |  | I31 |  | I33 |  | I35 |  | COM1
|  | I01 |  | I03 |  | I05 |  | I07 |  | I09 |  | I11 |  | I13 |  | I15 |  | I17 |  | I18 |  | I20 |  | I22 |  | I24 |  | I26 |  | I28 |  | I30 |  | I32 |  | I34 |  | 24G |  | 24V
Output | AC100-240 |  |  |  | Q00 |  | Q01 |  | Q02 |  | - |  | Q04 |  | Q06 |  | - |  | Q08 |  | Q10 |  | - |  | Q12 |  | Q14 |  | - |  | Q16 |  | Q18 |  | - |  | Q20 |  | Q22
|  | FG |  | COM0 |  | COM1 |  | COM2 |  | Q03 |  | COM3 |  | Q05 |  | Q07 |  | COM4 |  | Q09 |  | Q11 |  | COM5 |  | Q13 |  | Q15 |  | COM6 |  | Q17 |  | Q19 |  | COM7 |  | Q21 |  | Q23
3

## ADHA (GM7)
4. Analog Input/Output unit(G7F-ADHA)(GM7)
1. Performance Specification
| Items |  | Specifications
|  | No. of Input channels | 2
| Analog | Input Voltage range | DC0∼10V (input resisitance over than 1㏁)
| input | Input Current range | DC 0∼20mA | Classified by FB
| (A/D) |  | DC 4 ~ 20mA | (Input resisitance 250Ω)
|  | Resolution | 12bits(-48 ~ 4047)
|  | V/I Selection | With the Jumper(upper: V, lower: I)
|  | Allowable Input Range | DC 0∼+12V
DC 0∼+24mA
|  | No. of Output channels | 1
| Analog | Output Voltage range | DC 0∼10V(Load Resistance:1kΩ∼2㏁)
| output | Output Current range | DC 0∼20mA | Classified by FB
|  |  | DC 4 ~ 20mA | (Load Resistance less than 510Ω)
| (D/A) | Resolution | 12bits(-48 ~ 4047)
|  | V/I Selection | Select V or I Terminals
|  | Allowable output Range | DC 0∼+12V
DC 0∼+24mA
| Max. Resolution |  | DC 0∼10V : 2.5mV(1/4000)
DC 0∼20mA : 5㎂(1/4000)
DC 4∼20mA : 6.25㎂(1/3200)
| Overall Accuracy |  | ±0.5% in full scale
| Max. conversion speed |  | 2ms/ch. + scan time
| Internal currunt comsumption |  | 20mA
| Supply voltage |  | External DC 21.6V ~ 26.4V, 80mA
| Insulation |  | Photocoupler(Not insulated between the channels)
2. Function Blocks
|  | Reading Analog Input Data | ADHA_RD | DC0~10V, DC0 ~ 40mA Input Only
|  |  | AD420 | DC4 ~ 20mA Input Only
|  | Writing Analog Output Data | DAHA_WR | DC0 ~10V, DC0 ~ 40mA Output Only
|  |  | DA420 | DC4 ~ 20mA Output Only
|  | REQ : Enabling the FB |  |  | REQ : Enabling the FB
|  | SLOT : Slot No.(1~3) |  |  | SLOT : Slot No.(1~3)
|  | CH : Channel No.(0~1) |  |  | CH : Channel No.(0~1)
|  | V_I : 0(Current) |  |  | DONE : Normal Execution
|  | 1(Voltage) |  |  | STAT : Error Code
|  | DONE : Normal Execution |  |  | DATA : Digitalized Analog Input
STAT : Error Code
DATA : Digitalized Analog Input
4
|  | REQ : Enabling the FB |  |  | REQ : Enabling the FB
|  | SLOT :Slot No.(1~3) |  |  | SLOT : Slot No.(1~3)
|  | VI : 0(Current) |  |  | DATA : Digitalized
|  | 1(Voltage) |  |  | Analog Output
|  | DATA : Digitalized |  |  | DONE : Normal Execution
|  | Analog Output |  |  | STAT : Error Code
DONE :Normal Execution
STAT : Error Code
| Error code | Contents |  |  | Measures
| 0 | Normal operation
| 3 | Exceed the range of slot No. |  |  | Correct the slot No.
| 4 | No AD2A on the designated slot |  |  | Correct the slot No.
| 5 | Different type of module on the designated slot |  |  | Connect the slot No.
| 6 | Exceed the range of channel no. |  |  | Connect the Channel No.
3. Wiring examples
5
I
I
GND
V
V
GND
Voltage output
2K~1㏁
below
510Ω
Input
+
-
+
-
Voltage input
Current input
Terminal
block
Terminal
block
Input
Terminal
block
Terminal
block
Current output
V0
I0
COM0
V1
COM1
I1

## AD2A (GM7)
5. Analog Input unit(G7F-AD2A, 4ch, CPU v1.3)
1. Performance Specification
| Items |  | Specifications
|  | No. of Input channels | 4
| Analog | Input Voltage range | DC0∼10V (input resisitance over than 1㏁)
| input | Input Current range | DC 0∼20mA | Classified by FB
| (A/D) |  | DC 4 ~ 20mA | (Input resisitance 250Ω)
|  | Resolution | 12bits(-48 ~ 4047)
|  | V/I Selection | With the Jumper(left : V, right: I)
|  | Allowable Input Range | DC +/- 15V
DC +/- 25mA
| Max. Resolution |  | DC 0∼10V : 2.5mV(1/4000)
|  |  | DC 0∼20mA : 5㎂(1/4000) |  |  | Voltage | Current
DC 4∼20mA : 5㎂(1/3200)
| Overall Accuracy |  | ±0.5% in full scale
| Max. conversion speed |  | 2ms/ch. + scan time
| Internal currunt comsumption |  | 5V:20mA, +15V:100mA, -15V: 50mA
| Supply voltage |  | DC 21.6V ~ 26.4V, 100mA
| Insulation |  | Photocoupler(Not insulated between the channels)
2. Function Blocks
|  | Reading Analog data | AD2_RD | DC0~10V, DC0 ~ 20mA 개별 읽기
|  |  | AD2A_RD | DC0 ~10V, DC0~20mA 일괄 읽기
|  |  | AD2_420 | DC4 ~ 20mA 개별 읽기
|  |  | AD2A_420 | DC4 ~ 20mA 일괄 읽기
|  | REQ : Enabling the FB |  | REQ : Enabling the FB
|  | SLOT : Slot No.(1~3) |  | SLOT : Slot No.(1~3)
|  | CH : Channel No.(0~3) |  | CH : Channel No.(Array)
|  | V_I : 0(Current), 1(Voltage) |  | V_I : 0(Current), 1(Voltage)
|  | DONE : Normal Execution |  | DONE : Normal Execution
|  | STAT : Error Code |  | STAT : Error Code
|  | DATA : Digitalized Analog Input |  | DATA : Digitalized Analog Input
(Array variable )
|  | REQ : Enabling the FB |  | REQ : Enabling the FB
|  | SLOT : Slot No.(1~3) |  | SLOT : Slot No.(1~3)
|  | CH : Channel No.(0~3) |  | CH : Channel No.(0~3)
|  | DONE : Normal Execution |  | DONE : Normal Execution
|  | STAT : Error Code |  | STAT : Error Code
|  | DATA : Digitalized Analog Input |  | DATA : Digitalized Analog Input
(Array variable)
6
| Error code | Contents |  |  | Measures
| 0 | Normal operation
| 3 | Exceed the range of slot No. |  |  | Correct the slot No.
| 4 | No AD2A on the designated slot |  |  | Correct the slot No.
| 5 | Different type of module on the designated slot |  |  | Connect the slot No.
| 6 | Exceed the range of channel no. |  |  | Connect the Channel No.
3. Wiring examples
|  | Voltage input |  | Current input
|  | Input | Input
|  | Terminal |  |  | Terminal
7
+
-
+
-
V0
I0
COM0
V1
COM1
I1
CH.3
CH.2
CH.1
CH.0

## AT (GM7)
6. Analog timer(G7F-AT2A)(GM7)
1. Performance Specification
| Items | Specifications
| No. of channels | 4
| Digital output | 8bits(0 ~ 200)
| Setting method | Variable resistor(Potentiometer)
| Overall Accuracy | ±0.2% in full scale
| Internal currunt comsumption | 50mA
| No. of modules | Max. 3 modules connectable
2. Function Blocks
REQ : Enabling the FB
SLOT : Slot No.(1~3)
CH : Channel No.(0~3)
DONE : Normal Execution
STAT : Error Code
DATA : Digitalized Input (0~200)
8

## HSC (GM7)
7. A built-in High Speed Counter(GM7)
1. Performance Specifications
|  | Items |  | Specifications
|  | No. of Counters |  | 1 (1Φ or 2Φ)
|  | Counting Speed |  | 16kpps(1Φ) or 8kpps(2Φ)
|  | Counting Range |  | 0 ~ 16,777,215(24bit) UP/DOWN Count
|  | Input Contact |  | I00( AΦ), I01( BΦ), I02(Preset), COM
|  | Input Signal |  | DC24V/15mA
2. Function Blocks
|  | CHSC_WR |  |  | CHSC_RD
|  |  | REQ : Enabling the FB |  |  | REQ : Enabling the FB
|  |  | PHS : 0(1Φ Operation) |  |  | DONE : Normal Execution
|  |  | 1( 2Φ Operation) |  |  | STAT : Error Code
|  |  | MULT : Multiplication(1, 2 or 4) |  |  | CNT : Current Value of Counter
|  |  | U/D_I/E : Up/Down Selection |  |  | CY : Carry Flag(0 : OFF, 1 : ON)
0 : Selected by FB(DOWN)
1 : Selected by B Φ
BΦ:ON = Up
BΦ:OFF = Down
CY_R : Carry Reset Signal
1: Reset
DOWN : 0(Up Counting)
1(Down Counting under the condition of PHS=0 and U/D_I/E=0)
CT_E : Counter Enable Signal( 0: Disable, 1: Enable)
PRE_I/E : Preset Selection
0 : Preset by FB(CHSC_PRE), 1 : Preset by External Input(I02)
DONE : Normal Execution
STAT : Error Code(02: MULT data error in 2Φ Operation, not one of 1, 2 and 4)
- U/D_I/E and DOWN inputs are used for 1Φ Operation only.
- MULT input is used for 2Φ Operation only.
- When the CT_E input become 0, the current value is cleared to 0.
|  | CHSC_PRE |  |  | CHSC_SET(Used for Task Program only)
|  |  | REQ : Enabling the FB |  |  | REQ : Enabling the FB
|  |  | PSET : Preset Value |  |  | SET : Setting Value to be compared
|  |  | DONE : Normal Execution |  |  | DONE : Normal Execution
|  |  | STAT : Error Code |  |  | STAT : Error Code
|  |  | (03: out of range of PSET) |  |  | (03: out of range of SET)
(04: CHSC_PRE FB is excuted while the HSC is disabled state.)
- In case that the PRE_I/E input of CHSC_WR FB is 0, at the rising edge of REQ input of CHSC_PRE
the current value is changed into PSET value.
- In case that the PRE_I/E input of CHSC_WR FB is 1, at the rising edge of external input(I02)
the current value is changed into PSET value.(the REQ input of CHSC_PRE is ignored)
9
3. Task Program
A Task program can be executed when the current counting value reatches to the Setting value.
In this case, Task definition is necessary.
[7 empty] | 10 | 8

## Pulse output
8. Built-in Pulse output Function(GM7)
1. Performance Specifications
This function can be applied to Transistor output modules only.
|  | Items |  | Specifications
|  | No. of simultaneous |  | 1 output
|  | pulse output |  | (if not simultaneous, several pulse outputs available)
|  | Output speed |  | Max. 2kpps, Min. 50pps(in 50pps unit)
|  | No. of output pulses |  | 0 ~ 4,294,967,295
|  | Acc/Deceleration |  | Acc/Dec ratio
|  | Directon |  | Direction output or reverse pulse train output
|  | Rating load voltage |  | 12V/24V
|  | Operation voltage |  | DC10.2 ~ 26.4V
|  | Max. load current |  | 150mA
2. Wiring Example
|  | ① | Q00 | Pulse train output
|  | ② | COM0 | Pulse output common
|  | ③ | Q01 | Direction output
|  | ④ | COM1 | Direction output common
[Error Code]
00 : In normal state
01 : In pulse output state
02 : Speed setting error(not in unit of 50)
03 : No.of pulses of acc./dec is larger than that of total pulses
04 : Mismatched the pulse output contact
05 : Mismatched the direction output contact
11
3. Function Blocks
REQ : Request to execute the function block (operating by rising edge)
AEC_EN : Designation of increasing/decreasing velocity operation
0: constant velocity operation
1: increasing/decreasing velocity operation
AEC_NO : Slope of Increasing/decreasing operating
MAX_SPED : Maximum pulse output frequency(50 ~ 2000pps by unit of 50)
PLS_NO : No. of output pulses (0 ~ 4,294,967,295)
OUT_SLOT : Slot number of the pulse output contact
OUT_NO : Pulse output contact number
DIR_EN : Enabling the direction output ( 0:Disable, 1: Enable)
DIR_SLOT : Slot number of thevdirection signal output
DIR_NO : Direction signal output contact number
DIR_DATA : Direction output data(0: Forward, 1: Reverse)
CONTINUE : Enabling Infinite operation
0: Disable(Fixed or INC./DEC. velocity operation)
1: Infinite operation
EMG_STOP : Stop Signal
Immediately stop without decreasing time
RUN : RUN state
0: Stop the pulsating, 1: During pulsating
END : STOP state
0: During pulsating, 1: Stop the pulsating
CUR_CNT : Current value of output pulses
STAT: Error code
00: Normal state
01: Other PLS_OUT FB operating(pulsating)
02: Velocity setting error(set 0, over than 2000, not a multiple of 50)
03: The sum of Acc. and dec. pulses is over than that of total pulses.
04: Wrong assignment of the pulse output contact.
05: Wrong assignment of the direction output contact.
#. Operation Mode
A. Traprzoidal operation
constant
|  |  | acceleration |  |  |  | deceleration
B. Constant velocity operation
C. Infinite operation
Emergency stop
12
3. Program example
1) Operation
|  |  |  | ON |  | OFF
13
①
②
③
Pulse train output
AC100-240V
FG
COM0
Q00
COM1
Q01
COM2
Direction
Drive
Stepping motor
Time
Speed
Acc. ratio : 1
Dec. ratio : 1
Target speed = 1000pps
Start point
Target position=5000 pulse
(Operation pattern)
Forward
Reverse
Pulse output
(%Q0.0.0)
Direction
(%Q0.0.1)

## Pulse catch
9. Pulse catch inputs(GM7)
1. Function
This function can capture fast inputs with width as short as 0.2ms that cannot
normally be detected during the normal input cycling.
Max. eight(8) different pulse catch inputs(I00 ~I07) are available and configured
in the basic Parameter setting with GMWIN programming software.
Pulse input
Internal
Image
data
2. Parameter setting
14
Scan 1
Scan 2
Scan 3

## Inputfilter
10. Input filters(GM7)
1. Function
The inputs with filter prevent the CPU from reading abnormal inputs
and reduce the possibilities of input malfunction.
The filter time can be set in the range of 0 to 15ms in 1ms unit.
The set filter time is applied to all inputs except HSC, Pulse catch inputs.
The basic Parameter setting with KGLWIN programming software is needed for this.
2. Parameter setting
15
Input signal
Input
image data
time
Filter time
Filter time
Input
image data
Input signal

## RTC
11. Real Time Clock(GM7)
The RTC option module(G7E-RTCA) provides us with the Real Time.
(year, month, date, hour, minute, second, day)
The RTC data is stored in system flag [_RTC_TIME] with array varialble[8] of byte.
| RTC[0] | Lower two digits of the year
| RTC[1] | Month
| RTC[2] | Date
| RTC[3] | Hour
| RTC[4] | Minute
| RTC[5] | Second
| RTC[6] | Day(0:Mon ~ 6:Sun)
| RTC[7] | Higher two digits of the year
16
System Flag

## option
12. Option Units(GM7)
Digital I/O |  | G7E-DR10A |  | .I/O points
module |  |  |  | 6 DC inputs / 4 relay outputs
A/D·D/A |  | G7F-ADHA |  | .A/D : 2 channel , D/A : 1 channel
Analog timer |  | G7F-AT2A |  | .Input Points : 4points
Digital output range : 0~200
Cnet I/F module |  | G7L-CUEB |  | .RS-232C:1 channel |  | Not available for
|  | G7L-CUEC |  | .RS-422 :1 channel |  | G7M-xx10S
RTC module |  | G7E-RTCA |  | .Real Time Clock
Memory Module |  | G7M-M256 |  | .Back-up Memory 256Kbytes
BASE |  |  | 1st |  | 2nd |  | 3rd
UNIT |  |  | EXP. |  | EXP. |  | EXP.
|  |  | UNIT |  | UNIT |  | UNIT
G7E-RTCA
G7M-M256
G7E-DR10A | Max. 2units |  | Total 3 units can
G7F-ADHA | Max. 2units |  | be connected.
G7F-AD2A | Max. 2units
G7F-AT2A | Max. 3units
G7L-CUEB
G7L-CUEC
G7L-DUEA | Max. 1 of |  | under development
G7L-PBEA | these units |  | under development
G7L-FUEA
#. Only one(1) communiction channel is available.
(Loader Port(4,6,7pin), CUEB or CUEC)
17
25