Chapter 3  General Specifications 

Chapter 3. General Specifications 
	3.1 General Specifications


The following table shows the general specifications of the XGT Panel.
	No.
	Item
	Specifications
	References

	1
	Operating ambient

Temperature
	0 ~ 40 (C
	

	2
	Storage ambient

Temperature
	(10 ~ (50 (C
	

	3
	Operating ambient

Humidity
	5 ~ 95%RH, non-condensing
	

	4
	Storage ambient

Humidity
	5 ~ 95%RH, non-condensing
	

	5
	Vibrations
	Occasional vibration
	-
	

	
	
	Frequency
	Acceleration
	Amplitude
	Sweep count
	IEC 61131-2

	
	
	10 ( f ( 57Hz
	(
	0.075mm
	10 times for each

X, Y, Z axis
	

	
	
	57 ( f ( 150Hz
	9.8m/s2 {1G}
	(
	
	

	
	
	Continuous vibration
	
	

	
	
	Frequency
	Acceleration
	Amplitude
	
	

	
	
	10 ( f ( 57Hz
	(
	0.035mm
	
	

	
	
	57 ( f ( 150Hz
	4.9m/s2 {0.5G}
	(
	
	

	6
	Shocks
	( Maximum shock acceleration: 147 m/s2 {15G}

( Duration time: 11ms

( Pulse wave: half sine pulse ( 3 shocks per axis, on X, Y, Z axis )
	IEC 61131-2

	7
	Noise Immunity
	Square wave 

Impulse noise
	( 1,500 V
	LGIS’ Internal

Standard 

	
	
	Electronic discharge
	Voltage: 4 kV ( Discharge by contact )
	IEC 61131-2,

IEC 1000-4-2

	
	
	Radiated electromagnetic field noise
	27 ~ 500 MHz, 10 V/m
	IEC 61131-2,

IEC 1000-4-3

	
	
	Fast transient &

burst noise
	Voltage
	1kV

/ 0.25kV
	IEC 61131-2

IEC 1000-4-4

	8
	Atmosphere
	Free of corrosive gases and excessive dust
	

	9
	Altitude
	Up to 2,000m 
	

	10
	Pollution degree
	2 
	

	11
	Cooling method
	Air-cooling
	



	3.2 Performance Specifications


The following table shows the performance specifications of the XGT Panel

	Item
	Specifications
	References

	
	XP10BKA/DC
	XP10BKB/DC
	

	Input Voltage
	5V DC
	DC 4.9 ~ 5.1 (RS-232C Port)
	

	
	24V DC
	DC 21.6 ~ 26.4 ( DC Input connector)
	

	
	Consumption
current
	Less than 200mA
	

	Display
	LED Back-Light(192 x 64 Dot)
	

	Communication Interface
	RS-232C, RS-422/485
	Independent 2Ch

	Flash Memory
	256KByte
	

	RTC
	None
	Supports
	

	Download Specification
	115,200bps 
	

	Key 
	12Key(F1~f4, ESC, ALM, ▲,▼,◀,▶, SET, ENT)
	

	System Memory
	Read/Write
	M000 ~ M899 ( 900Word)
	

	
	Read only
	M9000 ~ M999(100Word)
	System flag












































































































































































































































































































































































































































REMARK








1) IEC (International Electrotechnical Commission): An international civilian institute who establishes international standards in area of electric and electronics.


2) Pollution degree: An indicator, which indicates pollution degree, which determine insulation performance of equipment.


* Pollution degree 2 : Normally, only non-conductive pollution occurs. Occasionally, however, a temporary conductivity caused by condensation shall be expected.



























































































































































































































































































































































































































































































































































































































































































































































































































































































































































PAGE  
3-2

