Chapter 3. General Specifications

3.1 General Specifications

The following table shows the general specifications of the XGT Panel.

| No. | Item | Specifications |  |  |  |  |  | References |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating ambient Temperature | 0 ~ 40 C |  |  |  |  |  |  |
| 2 | Storage ambient Temperature | 10 ~ 50 C |  |  |  |  |  |  |
| 3 | Operating ambient Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 4 | Storage ambient Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 5 | Vibrations | Occasional vibration |  |  |  |  | - |  |
|  |  | Frequency |  | Acceleration |  | Amplitude | Sweep count | IEC 61131-2 |
|  |  | 10  f  57Hz |  |  |  | 0.075mm | 10 times for each X, Y, Z axis |  |
|  |  | 57  f  150Hz |  | 9.8m/s2 {1G} |  |  |  |  |
|  |  | Continuous vibration |  |  |  |  |  |  |
|  |  | Frequency |  | Acceleration |  | Amplitude |  |  |
|  |  | 10  f  57Hz |  |  |  | 0.035mm |  |  |
|  |  | 57  f  150Hz |  | 4.9m/s2 {0.5G} |  |  |  |  |
| 6 | Shocks |  Maximum shock acceleration: 147 m/s2 {15G}  Duration time: 11ms  Pulse wave: half sine pulse ( 3 shocks per axis, on X, Y, Z axis ) |  |  |  |  |  | IEC 61131-2 |
| 7 | Noise Immunity | Square wave Impulse noise |  1,500 V |  |  |  |  | LGIS’ Internal Standard |
|  |  | Electronic discharge | Voltage: 4 kV ( Discharge by contact ) |  |  |  |  | IEC 61131-2, IEC 1000-4-2 |
|  |  | Radiated electromagnetic field noise | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC 61131-2, IEC 1000-4-3 |
|  |  | Fast transient & burst noise | Voltage |  | 1kV / 0.25kV |  |  | IEC 61131-2 IEC 1000-4-4 |
| 8 | Atmosphere | Free of corrosive gases and excessive dust |  |  |  |  |  |  |
| 9 | Altitude | Up to 2,000m |  |  |  |  |  |  |
| 10 | Pollution degree | 2 |  |  |  |  |  |  |
| 11 | Cooling method | Air-cooling |  |  |  |  |  |  |

1) IEC (International Electrotechnical Commission): An international civilian institute who establishes international standards in area of electric and electronics.

2) Pollution degree: An indicator, which indicates pollution degree, which determine insulation performance of equipment.

* Pollution degree 2 : Normally, only non-conductive pollution occurs. Occasionally, however, a temporary conductivity caused by condensation shall be expected.

#### REMARK

3.2 Performance Specifications

The following table shows the performance specifications of the XGT Panel

| Item |  |  | Specifications |  | References |
| --- | --- | --- | --- | --- | --- |
|  |  |  | XP10BKA/DC | XP10BKB/DC |  |
| Input Voltage | 5V DC |  | DC 4.9 ~ 5.1 (RS-232C Port) |  |  |
|  | 24V DC |  | DC 21.6 ~ 26.4 ( DC Input connector) |  |  |
|  | Consumption current |  | Less than 200mA |  |  |
| Display |  |  | LED Back-Light(192 x 64 Dot) |  |  |
| Communication Interface |  |  | RS-232C, RS-422/485 |  | Independent 2Ch |
| Flash Memory |  |  | 256KByte |  |  |
| RTC |  |  | None | Supports |  |
| Download Specification |  |  | 115,200bps |  |  |
| Key |  |  | 12Key(F1~f4, ESC, ALM, ▲,▼,◀,▶, SET, ENT) |  |  |
| System Memory |  | Read/Write | M000 ~ M899 ( 900Word) |  |  |
|  |  | Read only | M9000 ~ M999(100Word) |  | System flag |