#### Chapter 10 Maintenance and Repair

To maintain the PLC in the optimal status, please carry out daily check and regular check.

10.1 Repair and Check

I/O module is composed usually of semiconductor microelectronic device and the life is semi-   permanent. As the microelectronic device may occur the error caused by the ambient environment, it is required to check periodically. The following is the items to be checked 1~2 times every 6 months.

| Check items |  | Judgment basis | Action |
| --- | --- | --- | --- |
| Ambient environment | Temperature | 0 ~ +55C | Control the use temperature and the use humidity. |
|  | Humidity | 5 ~ 95%RH |  |
|  | Vibration | No vibration | Use the dust-proof rubber or take the vibration protection policy. |
| Shaking of each unit and module |  | No shake | Make all unit and module not to be shaked |
| Terminal screw loosened. |  | No loosening | Tighten the loosened screw. |
| Input voltage change rate |  | Within 15%/+10% | Maintain the change rate within the allowable range. |
| Spare parts |  | Check if the quantity of spare part and the preservation status is good. | Make up the insufficient and improve the preservation status. |

10.2 Daily Check

Daily checking point for Smart I/O module is as follows.

1) Daily check for Profibus-DP module

| Checking items |  | Description | Judgment basis | Action |
| --- | --- | --- | --- | --- |
| Cable connection status |  | Cable loosening | No loosening | Tighten the cable |
| Module connection status |  | Screw loosening | No loosening | Tighten the module screw. |
| Indication LED | RUN LED | Light ‘ON’ check | Steady-state of Power | Refer to Chapter 3. |
|  | RDY LED | Light ‘ON’ check | Steady-state of communica- tion module interface | Refer to Chapter 3. |
|  | ERR LED | Light ‘ON’ check | Abnormal communication H/W or cable check | Refer to Chapter 3. |

2) Daily check for DeviceNet module

| Checking items |  | Description | Judgment basis | Action |
| --- | --- | --- | --- | --- |
| Cable connection status |  | Cable loosening | No loosening | Tighten the cable |
| Module connection status |  | Screw loosening | No loosening | Tighten the module screw. |
| Indication LED | PWR LED | Light ‘ON’ check | Steady-state of Power | Refer to Chapter 3. |
|  | MS LED | Light ‘ON’ check | Steady-state of communication module interface (if abnormal, check the H/W or the cable) | Refer to Chapter 3. |
|  | NS LED | Light ‘ON’ check | Steady-state of communication module network (if abnormal, check Smart I/O H/W) | Refer to Chapter 3. |

3) Daily check for Rnet module

| Checking items |  | Description | Judgment basis | Action |
| --- | --- | --- | --- | --- |
| Cable connection status |  | Cable loosening | No loosening | Tighten the cable |
| Module connection status |  | Screw loosening | No loosening | Tighten the module screw. |
| Indication LED | PWR LED | Light ‘ON’ check | Steady-state of power | Refer to Chapter 3. |
|  | TX LED | Light ‘ON’ check | While sending/receiving with the master (if error occurs, check the H/W or the cable) | Refer to Chapter 3. |
|  | RX LED | Light ‘ON’ check | While communicating with Smart I/O, (if error occurs, check Smart I/O Hardware.) | Refer to Chapter 3. |

4) Daily check for Modbus module

| Checking items |  | Description | Judgment basis | Action |
| --- | --- | --- | --- | --- |
| Cable connection status |  | Cable loosening | No loosening | Tighten the cable |
| Module connection status |  | Screw loosening | No loosening | Tighten the module screw. |
| Indication LED | PWR LED | Light ‘ON’ check | Steady-state of power | Refer to Chapter 3. |
|  | TX LED | Light ‘ON’ check | Steady-state of communication module interface (if error occurs, check the H/W or the cable) | Refer to Chapter 3. |
|  | RX LED | Light ‘ON’ check | Steady-state of communication network (if error occurs, check Smart I/O hardware.) | Refer to Chapter 3. |

10.3 Regular Check

Check the following items 1~2 times every 6 months and take the necessary actions.

| Checking items |  | Checking method | Judgment basis | Action |
| --- | --- | --- | --- | --- |
| Ambient environment | Temperature | Measure by thermometer/hygrometer. | 0 ~ 55℃ | Adjust suitable for general standard (in case of using in the area, apply the environment basis in the area) |
|  | Humidity |  | 5 ~ 95%RH |  |
|  | Pollution | Measure the corrosive gas. | No corrosive gas |  |
| Module status | Loosening, shaking | Shake the communication module. | Tightening status | Tighten the screw. |
|  | Dust, foreign material adding | Macrography | No adding |  |
| Connection status | Terminal screw loosened | Tightening by the driver | No loosening | Tightening |
|  | Pressed terminal approach | Macrography | Proper interval | Correction |
|  | Connector loosened. | Macrography | No loosening | Connector correction Screw tightening |
| Power/voltage check |  | Voltage measure between terminals | AC 85 ~ 132V AC 170 ~ 264V | Power supply change |