# Function Block for Modbus Communication.

1. Features

- By using this function block, GLOFA Cnet module operates as a Modbus master on Modbus network.

- Supporting command codes are as below.

  - Read coil status: 01

  - Read input status: 02

  - Read holding registers: 03

  - Read input registers: 04

  - Force single coil: 05

  - Preset single register: 06

  - Force multiple coils: 15 (Hex 0F)

  - Preset multiple register: 16 (Hex 10)

- This function block works on user-define protocol mode of Cnet.

- Basic Communication parameters (Baudrate, Data bit, Stop bit, Parity check, Station No.) are set by

Cnet Editor and Frame editing is not required.

- Modbus RTU Protocol is supported (ASCII Protocol will be supported soon.)

- For using this function block, Cnet Module’s requirement is as below

  - Cnet module’s H/W version is higher than v2.0 (can be checked on GMWIN)

  - Cnet module’s Flash Rom OS version is higher than v1.01 (can be checked on Cnet Editor)

Modbus Master

Modbus Slave

Command

Response

Modbus (RS-422/485)

GLOFA CPU &

GnL-CUEA

Other Maker’s Device

5

6

7

9

8

4

3

2

1

0

Cnet communication mode should be

”User defined protocol mode”

2. Checking Cnet Flash Rom OS version.

- Run the frame editor and connect to the Cnet module.

- Select Flash Memory – Information in Online menu

Flash Rom Version should

be higher than v1.01

3. Upgrading Cnet Flash Rom OS (In case that version is lower than 1.01)

- Set the Cnet module to ‘Flash memory write mode’ (Mode 8) with the mode selection switch.

- RUN LED of Cnet module will blink with 1 second period

- Run the frame editor and connect to the Cnet module.

- Select ‘F6OS.BIN’ (Cnet OS for G6L-CUEA) or ‘F34OS.BIN’ (Cnet OS for G3L-CUEA) in Open Lib

menu.

- Select Online – Flash Memory – Write in the menu, then type the slot number at which the Cnet

module is mounted, and press ‘Write’ button.

4. Parameter

- Basic Parameter

Frame editing is not required

Modbus Station No. of GLOFA

Communication specification

should be the same as that

of other station (Baudrate, Parity

Data bit, Stop bit)

5. Programming

- Library Inserting

- Copy “modbus.Nfb” file to lib directory of GMWIN

- Select “Project  Library insert” on GMWIN menu

- Click Add  then select “communi.Nfb” and “modbus.Nfb”

(N=6: G6L-CUEA,  N=4: G4L-CUEA,  N=3: G3L-CUEA)

- Function Block (RTU_RD, RTU_WR)

  - RTU_RD (Data read by using Modbus RTU protocol)

|  | IN / OUT | Type | Description |
| --- | --- | --- | --- |
|  | REQ | BOOL | Execution condition for function block (When condition changes 0 to 1, FB executes 1 time) * Refer to note 1 |
|  | SLOT | USINT | Slot Number cnet module installed (0 ~ 7) |
|  | CH | USINT | 0: RS-232C, 1: RS-422/485 |
|  | STN | USINT | Destination station to be read (0 ~ 32) |
|  | CMND | USINT | Modbus Function command (1 ~4) 1: Read coil status (Bit) 2: Read input status (Bit) 3: Read holding register (Word) 4: Read input register (Word) |
|  | ADDR | INT | Head address to be read (0 ~ 65535) |
|  | NUM | USINT | Number of data to be read (1 ~ 64) |
|  | RES_WAIT | TIME | Response wait time (After waiting for the time to be set, PLC CPU read the response from Cnet module) * Refer to note 2 |
|  | NDR | BOOL | Holds ‘ON’ status during 1 scan after communication Is completed successfully |
|  | ERR | BOOL | Holds ‘ON’ status during 1 scan after communication Is completed abnormally |
|  | STATUS | USINT | Communication status code (Error code) 0: Normal, Not 0: Error code * Refer to note 3 |
|  | DATA | USINT ARRY (256) | Area which received data is stored. Array [0]: High Byte of 1st received word. Array [1]: Low Byte of 1st received word. Array [2]: High Byte of 2nd received word. Array [3]: Low Byte of 2nd received word. …. |

  - MBUS_WR (Data write by using Modbus RTU protocol)

|  | IN / OUT | Type | Description |
| --- | --- | --- | --- |
|  | REQ | BOOL | Execution condition for function block (When condition changes 0 to 1, FB executes 1 time) * Refer to note 1 |
|  | SLOT | USINT | Slot Number cnet module installed (0 ~ 7) |
|  | CH | USINT | 0: RS-232C, 1: RS-422/485 |
|  | STN | USINT | Destination station to be written (0 ~ 32) |
|  | CMND | USINT | Modbus Command 05: Force single coil (Bit) 06: Preset single register (Word) 15: Force Multiple coils (Bit) 16: Preset Multiple register (Word) |
|  | ADDR | INT | Head address to be written (0 ~ 65535) |
|  | NUM | USINT | Number of data to be written (1 ~ 64) * When using command 5 or 6 this value will be ignored. |
|  | RES_WAIT | TIME | Response wait time (After waiting for the time to be set, PLC CPU read the response from cnet module) * Refer to note 2 |
|  | NDR | BOOL | Holds ‘ON’ status during 1 scan after communication Is completed successfully |
|  | ERR | BOOL | Holds ‘ON’ status during 1 scan after communication Is completed abnormally |
|  | STATUS | USINT | Communication status code (Error code) 0: Normal, Not 0: Error code * Refer to note 3 |
|  | DATA | USINT ARRY (256) | Area which writing data is stored. Array [0]: High Byte of 1st writing word. Array [1]: Low Byte of 1st writing word. Array [2]: High Byte of 2nd writing word. Array [3]: Low Byte of 2nd writing word. …. * When using command 05. Array [0] = 1  ON Array [0] = 0  OFF |

♠ Note 1

## Execution Condition

- Execution condition (REQ) of RTU_RD / RTU_WR should be turned on, after previous

execution have been completed successfully. (after ‘NDR’ have been turned on)

REQ

NDR

Communicating time = Internal processing time + response wait time

(Internal processing time: 50 ~ 60ms)

Previous request

Next request

♠ Note 2

### Response Wait Time

- After waiting for the time to be set, PLC CPU read the response from cnet module

- This value can be related with received data size, transmission speed (Baudrate) and

other station’s responding performance.

- Recommended minimum value is as below. (When an error occurs with this value,

make the value longer.)

| Request data size Baudrate | 1 ~ 16 word | 17 ~ 32 word | 33 ~ 48 word | 49 ~ 64 word |
| --- | --- | --- | --- | --- |
| 4800 bps | 150ms | 250ms | 330ms | 400ms |
| 9600 bps | 100ms | 180ms | 230ms | 280ms |
| 19200 bps | 80ms | 150ms | 180ms | 230ms |

♠ Note 3

### Status Code

- Status code indicates communication status

| Status code (Dec) | Description | Solution | Remarks |
| --- | --- | --- | --- |
| 0 | Normal | No error |  |
| 1 | Illegal command (Not allowable Command was requested to the slave) | 1. Check the allowable command for the slave then change the command code In function block | Returning value from slave |
| 2 | Illegal address (Not allowable address was requested to the slave) | 1. Check the allowable address for the slave then change the address In function block |  |
| 3 | Illegal data value (Not allowable data value was requested to the slave) | 1. Check the allowable data range for the slave then change the data value In function block |  |
| 4 | Slave device failure (An unrecoverable error occurred while the slave was attempting to perform the requested action) | 1. Check the slave status |  |
| 6 | Slave device busy | 1. Execute function block again later when the slave is free. |  |
| 10 | Received Frame CRC error | 1. Make the response wait time longer than previous value. 2. Check the cable and frame status | Value generated by function block |
| 17 or 16 | Cnet module I/F error | 1. Check the slot no. designated on function block |  |
| 21 or 64 | Channel(232c/422) stop | 1. Make the cnet module run mode. |  |
| 74 | Time out error | 1. Check the basic parameter 2. Check destination the station no. 3. Check the cable status |  |
| 21 or 115 | Communication mode error | 1. Check the cnet mode then select user define protocol mode. |  |
| 255 | FB input parameter error | 1. Check the FB input value. (Slot,CH,Command,Number etc) |  |

6. Example

♠ Communication between GLOFA GM6 and Inverter IG5

- Inverter Operation Command

- Using Command 16 (Preset Multiple register: Word).

%MB400 ~%MB655

(%MW200~%MW327)

- Inverter Operation Monitor

- Using Command 03 (Read holding register: Word).

%MB0~%MB255

(%MW0~%MW127)