Chapter 2 Product Specification

2.1 General Specification

The General Specification of Smart I/O series is as follows.

| No | Items | Specification |  |  |  |  |  |  |  |  | References |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Use temperature | 0 ~ 55 C |  |  |  |  |  |  |  |  |  |
| 2 | Storage Temp. | 25 ~ 70 C |  |  |  |  |  |  |  |  |  |
| 3 | Use humidity | 5 ~ 95%RH, no dew |  |  |  |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, no dew |  |  |  |  |  |  |  |  |  |
| 5 | Vibration-resistant | In case of Intermittent vibration |  |  |  |  |  |  |  | - |  |
|  |  | Frequency |  | Acceleration |  |  |  | Amplitude |  | Times | IEC6 1131-2 |
|  |  | 10  f  57Hz |  |  |  |  |  | 0.075mm |  | X, Y, Z 10 times each direction |  |
|  |  | 57  f  150Hz |  | 9.8m/s2{1G} |  |  |  |  |  |  |  |
|  |  | In case of Continuous vibration |  |  |  |  |  |  |  |  |  |
|  |  | Frequency |  | Acceleration |  |  | Amplitude |  |  |  |  |
|  |  | 10  f  57Hz |  |  |  |  | 0.035mm |  |  |  |  |
|  |  | 57  f  150Hz |  | 4.9m/s2{0.5G} |  |  |  |  |  |  |  |
| 6 | Impact-proof |  max. impact acceleration : 147 m/s2{15G}  Application time : 11ms  pulse wave type : semi-sine wave pulse (3 times each direction X, Y, Z) |  |  |  |  |  |  |  |  | IEC 61131-2 |
| 7 | Noise-resistant | Square wave impulse noise | AC :  1,500 V, DC : 900 V |  |  |  |  |  |  |  | LG산전내부 시험규격기준 |
|  |  | Electrostatic discharge | Voltage : 4kV (Touch discharge) |  |  |  |  |  |  |  | IEC 61131-2, IEC 801-2 |
|  |  | Radiant electromagnetic field noise | 27 ~ 500 MHz, 10 V/m |  |  |  |  |  |  |  | IEC 61131-2, IEC 801-3 |
|  |  | Fast Transient / Bust Noise | Classification |  | Power module | Digital I/O (more than 24V ) |  |  | Digital I/O (below 24V) Analog I/O Communication Interface |  | IEC 61131-2 IEC 801-4 |
|  |  |  | Voltage |  | 2kV | 1kV |  |  | 0.25kV |  |  |
| 8 | Surrounding environment | No corrosive gas, no dust |  |  |  |  |  |  |  |  |  |
| 9 | Use altitude | Less than 2,000m |  |  |  |  |  |  |  |  |  |
| 10 | Pollution | Less than 2 |  |  |  |  |  |  |  |  |  |
| 11 | Cooling method | Natural air-conditioning |  |  |  |  |  |  |  |  |  |

1) IEC(International Electrotechnical Commission)

: International civil community that promotes international cooperation for standardization of electric/ electro technology, publishes international standard and operates suitability assessment system related to the abov.

2) Pollution Degree

: An index that indicates the pollution degree of used environment that determines the insulation performance of the device. For example, pollution degree 2 means the state to occur the pollution of non-electric conductivity generally, but the state to occur temporary electric conduction according to the formation of dew.        .

###### Remark

# 제 4장 CPU모듈

2.2 Power Specification

Here describes the Power Specification of Smart I/O.

### 2.2.1 Performance Specification

Here describes Power Performance Specification of Smart I/O Profibus-DP(Pnet) module.

| Items | Specification |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | GPL- TR2A | GPL- TR4A | GPL- RY2A | GPL- DT4A | GPL- D22A | GPL- D24A |
| Input power | DC +24V (Max +28V, Min +19V) |  |  |  |  |  |
| Input current | 0.4A(+24VDC) |  |  |  |  |  |
| Dash current | Less than 40A : (24VDC input) |  |  |  |  |  |
| Rated output current (+5V) | 0.2~0.6A |  |  |  |  |  |
| Rated output current (+5V, Aux) | 0.02~0.1A |  |  |  |  |  |
| Efficiency | More than 60% (in case of Full Load) |  |  |  |  |  |
| Power indication | When power input, LED ON |  |  |  |  |  |
| Output voltage dwell time | Within 150ms (DC19~24V input, Full Load) |  |  |  |  |  |
| Suitable wire spec | 1.5 ~ 2.5mm2 (AWG16 ~ 22) |  |  |  |  |  |
| Suitable tightening torque | 12kg  cm |  |  |  |  |  |

Here describes Power Performance Specification of Smart I/O DeviceNet, Rnet, Modbus module.

| Items | Specification |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | GD/R/SL- TR2A | GD/R/SL- TR4A | GD/R/SL- RY2A | GD/R/SL- DT4A | GD/R/SL- D22A | GD/R/SL- D24A |
| Input power | DC +24V (Max +28V, Min +19V) |  |  |  |  |  |
| Input current | 0.4A(+24VDC) |  |  |  |  |  |
| Dash current | Less than 40A : (24VDC input) |  |  |  |  |  |
| Rated output current (+5V) | 0.2~0.6A |  |  |  |  |  |
| Efficiency | More than 60% (in case of Full Load) |  |  |  |  |  |
| Power indication | When power input, LED ON |  |  |  |  |  |
| Output voltage dwell time | Within 150ms (DC19~24V input, Full Load) |  |  |  |  |  |
| Suitable wire spec | 1.5 ~ 2.5mm2 (AWG16 ~ 22) |  |  |  |  |  |
| Suitable tightening torque | 12kg  cm |  |  |  |  |  |

2.3 Digital Input Module Specification

2.3.1 DC16 point Input Module : GPL/GDL/GRL/GSL-D22A

| Type name Spec. |  | DC input module |
| --- | --- | --- |
| Input point |  | 16 points |
| Insulation method |  | Photo coupler insulation |
| Rated input voltage |  | DC24V |
| Rated input current |  | 7 mA |
| Use voltage range |  | DC20.4 ~ 28.8V (ripple rate : within 5% ) |
| Max. simultaneous input point |  | 100% (16 points/1COM) simultaneously ON |
| ON voltage / ON current |  | More than DC19V / more than 3.5 mA |
| OFF voltage / OFF current |  | Less than DC6V / less than 1.5 mA |
| Input resistance |  | Approx. 3.3 k |
| Response time | Off  On | Less than 3 ms |
|  | On  Off | Less than 3 ms |
| Common method |  | 16 points / COM |
| Internal consumption current |  | Less than 200mA |
| Action indication |  | LED ON when input ON |
| External connection method |  | Terminal unit connector (M3 X 6 screws) |
| weight |  | Less than 160g |
| Circuit Configuration R R DC24V 00 15 COM1 DC5V R R FG DC5V DC24V Power circuit Internal circuit Photo coupler |  |  |

2.3.2 DC32 point Input Module : GPL/GDL/GRL/GSL-D24A

| Type name Spec. |  | DC Input Module |
| --- | --- | --- |
| Input point |  | 32 points |
| Insulation method |  | Photo coupler insulation |
| Rated input voltage |  | DC24V |
| Rated input voltage |  | 7 mA |
| Use voltage range |  | DC20.4 ~ 28.8V (ripple rate : within 5% ) |
| Max. simultaneous input point |  | 100% (16 points/1COM) simultaneously ON |
| ON voltage / ON current |  | More than DC19V / more than 3.5 mA |
| OFF voltage / OFF current |  | Less than DC6V / less than 1.5 mA |
| Input resistance |  | Approx. 3.3 k |
| Response time | Off -> On | Less than 3 ms |
|  | On - > Off | Less than 3 ms |
| Common method |  | 16 points / COM |
| Internal consumption current |  | Less than 300 mA |
| Action indication |  | LED ON when input ON |
| External connection method |  | Terminal unit connector (M3 X 6 screws) |
| Weight |  | Less than 240g |
| Circuit Configuration R R DC24V 16 31 COM1 DC5V R R FG DC5V DC24V R R DC24V 00 15 COM0 DC5V R R Power circuit Internal circuit Internal circuit Photo coupler Photo coupler |  |  |

2.4 Digital Output Module Specification

2.4.1 16 point Relay Output Module : GPL/GDL/GRL/GSL-RY2A

| Type name Spec. |  | Relay Output Module |
| --- | --- | --- |
| Output point |  | 16 points |
| Insulation method |  | Relay insulation |
| Rated load voltage/current |  | DC24V 2A(resistance load) / 1point, AC220V 2A(COS = 1) |
| Min.(max.) load voltage/current |  | DC5V / 1mA, AC250V, DC110V |
| Max. open/close frequency |  | 1,200 times / hr |
| Surge killer |  | None |
| Life | Mechanical | More than 20,000,000 times |
|  | Electrical | Rated load voltage/current more than 100,000 times |
|  |  | AC200V / 1.5A, AC240V / 1A (COS = 0.7) more than 100,000 |
|  |  | AC200V / 1A, AC240V / 0.5A (COS = 0.35) more than 100,000 |
|  |  | DC24V / 1A, DC100V / 0.1A (L / R = 7ms) more than 100,000 |
| Response time | Off  On | Less than 10 ms |
|  | On  Off | Less than 12 ms |
| Common method |  | 8 points / COM |
| Internal consumption current |  | Less than 550 mA (when all points ON) |
| Action indication |  | LED ON when output ON |
| External connection method |  | Terminal unit connector (M3 X 6 screws) |
| Weight |  | Less than 300g |
| Circuit Configuration 5V COMC AC110/220V DC24V 00 DC5V L L Relay 07 TD62083 COMA 08 DC5V L L Relay 15 TD62083 DC24V FG AC110/220V DC24V AC110/220V DC24V AC110/220V DC24V Internal power Internal circuit Internal circuit Coil Coil |  |  |

2.4.2 16 point Transistor Output Module : GPL/GDL/GRL/GSL-TR2A

| Type name Spec. |  |  | Transistor Output Module |
| --- | --- | --- | --- |
| Output point |  |  | 16 points |
| Insulation method |  |  | Photo coupler insulation |
| Rated load voltage |  |  | DC 24V |
| Use load voltage range |  |  | DC 20.4 ~ 26.4V |
| Max. load current |  |  | 0.1A / 1point, 2A / 1COM |
| Leakage current when OFF |  |  | Less than 0.1mA |
| Max. inrush current |  |  | Less than 4A / 10 ms |
| Max. voltage falling when ON |  |  | DC 1.5V |
| Surge killer |  |  | Clamp diode |
| Response time | Off  On |  | Less than 2 ms |
|  | On  Off |  | Less than 2 ms |
| Common method |  |  | 16 points / 1COM |
| Internal consumption current |  |  | Less than 280 mA (when all points ON) |
| External power Supply |  | Voltage | DC24V  10% (ripple voltage : less than 4 Vp-p) |
|  |  | current | Less than 50 mA (DC24V per 1COM ) |
| Action indication |  |  | LED ON when output ON |
| External connection method |  |  | Terminal unit connector (M3 X 6 screws) |
| Weight |  |  | Less than 160g |
| Circuit Configuration 00 R L 15 L Transistor DC24V DC24V FG DC5V R COM R Internal circuit Power circuit Photo coupler |  |  |  |

2.4.3 32 point Transistor Output Module : GPL/GDL/GRL/GSL-TR4A

|  | Type name Spec. |  |  | Transistor Output Module |
| --- | --- | --- | --- | --- |
|  | Output point |  |  | 32 points |
|  | Insulation method |  |  | Photo coupler insulation |
|  | Rated load voltage |  |  | DC 24V |
|  | Use load voltage range |  |  | DC 20.4 ~ 26.4V |
|  | Max. load current |  |  | 0.1A / 1point, 2A / 1COM |
|  | Leakage current when OFF |  |  | Less than 0.1 mA |
|  | Max. inrush current |  |  | Less than 0.4 A / 10 ms |
|  | Max. voltage falling when ON |  |  | DC 1.0 V |
|  | Response time | Off  On |  | Less than 2 ms |
|  |  | On  Off |  | Less than 2 ms |
|  | Common method |  |  | 16 points / 1 COM |
|  | Internal consumption current |  |  | Less than 380 mA (when all points ON) |
|  | External power supply |  | Voltage | DC 24V  10 % (ripple voltage : less than 4Vp-p ) |
|  |  |  | current | 40 mA (DC 24V per 1 COM) |
|  | Action indication |  |  | LED ON when output ON (16 points indication conversion by selection switch) |
|  | External connection method |  |  | Terminal unit connector (M3 X 6 screws) |
|  | Weight |  |  | Less than 240g |
|  | Circuit Configuration 12 00 R L 15 L DC24V FG DC5V R COM1 L L 16 31 Transistor Transistor COM0 R R R R Power circuit Internal circuit Internal circuit Photo coupler Photo coupler |  |  |  |
| 2.5 Digital I/O Combined Module Specification |  |  |  |  |

2.5.1 32 point I/O Combined Module(DC16/TR16 point): GPL/GDL/GRL/GSL-DT4A

| I/O Combined Module |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Input |  |  | Output |  |  |
| Input point |  | 16 point | Output point |  | 16 point |
| Insulation method |  | Photo coupler insulation | Insulation method |  | Photo coupler insulation |
| Rated input voltage |  | DC 24V | Rated load voltage |  | DC24V |
| Rated input current |  | 7 mA | Max. load current |  | 0.1A/1point, 2A/1COM |
| Use voltage range |  | DC20.4~26.4V (ripple rate : within 5%) | Max. load voltage/current |  | AC250V, DC125V |
| Max. simultaneous input point |  | 100% simultaneously ON | Leakage current when OFF |  | Less than 0.1 mA |
| ON voltage/ON current |  | DC19V/3.0 mA or more | Max. inrush current |  | Less than 4A/10ms |
| OFF voltage/OFF current |  | DC6V/1.5 mA or less | Surge killer |  | none |
| Input resistance |  | Approx. 3.3 k | Response time | Off  On | Less than 2 ms |
| Response time | Off On | Less than 3 ms |  | On  Off | Less than 2 ms |
|  | On  Off | Less than 3 ms |  |  |  |
| Common method |  | 16 points / COM | Common method |  | 16 points / 1COM |
| Action indication |  | LED ON when input ON | Action indication |  | LED ON when output ON |
| External connection method |  | Terminal unit connector (M3×6 screws) |  |  |  |
| Internal consumption current |  | Less than 350 mA |  |  |  |
| Weight |  | Less than 240g |  |  |  |
| Circuit Configuration 00 R L 15 FG DC5V R L Transistor COM0 DC24V DC24V R R DC24V 00 15 COM1 DC5V R R R Power circuit Internal circuit Internal circuit Photo coupler Photo coupler |  |  |  |  |  |
| 2.6 Communication Module Specification |  |  |  |  |  |

2.6.1 Profibus-DP Module Specification

| Classification | Profibus-DP |
| --- | --- |
| Module Type | Remote slave |
| Standard | EN 50170 / DIN 19245 |
| Interface | RS-485(Electric) |
| Medium Access | POLL |
| Topology | BUS |
| Encoding method | NRZ |
| Cable | Shielded Twisted Pair |
| Communication distance | 1200m (9.6K ~187Kbps) |
|  | 400m (500 Kbps) |
|  | 200m (1.5 Mbps) |
|  | 100m (3M ~ 12Mbps) |
| Max. node | 126 stations |
| Max. node (per segment) | 32 stations |
| Max. I/O data | 64Byte |

2.6.2 DeviceNet Module Specification

| Classification |  | DeviceNet |
| --- | --- | --- |
| Module type |  | Remote slave |
| Protocol |  | CAN Protocol |
| Medium Access |  | POLL |
| Topology |  | BUS |
| Cable |  | Class 2 Thick/Thin Cable(Allen-Bradley standard) |
| Communication speed |  | 125/250/500 kbps |
| Communication distance(Thick) |  | 500/250/100 m |
| Max. drop length | 125 kbps | 6m(max. extension 156m) |
|  | 250 kbps | 6m(max. extension 78m) |
|  | 500 kbps | 6m(max. extension 39m) |
| Data packet |  | 0 ~ 8 Byte(64 Bits) |
| Network structure |  | Trunk/drop line Power within same network/ signal cable |
| Bus method |  | Multi slave/ multi casting Peer-to-Peer method Strobe,Poll,COS/Cyclic method |
| Max. node |  | Max. 64 MAC ID 32 I/O per node (max. 2,048 I/O) |
| System type |  | Node insertion/removal in voltage ON |
| Action voltage |  | DC 24V |

2.6.3 Rnet Module Specification

| Classification | Rnet |
| --- | --- |
| Allowable inspection power cut time | 20ms |
| Communication speed | 1Mbps |
| Communication method | Semi dual bit serial method |
| Synchronous method | Frame synchronous method |
| Transmission path method | BUS |
| Total extension distance | 750m |
| No. of connecting station | 64 stations (including master stations) |
| Modulation method | Manchester Biphase-L |
| Error control method | Retry by CRC-CCITT and Time Over |
| Connector connection | 9-PIN plug type |
| Using cable | TWISTED PAIR SHIELDED CABLE |
| Max. communication point | 3,840 Word (master base) |
| Max. sending point | 1,920 Word(master base) |
| Max. block no. assignment | 63 |
| Max. point of Block unit | 60 Word |

2.6.4 Modbus Module Specification

| Classification | Snet |
| --- | --- |
| Module type | Remote slave |
| Protocol | Modbus-RTU |
| Max. protocol size | 8 Byte |
| Topology | BUS |
| Cable | TWISTED PAIR SHIELDED CABLE |
| Communication speed | 2400 ~ 38,400 BPS |
| Communication distance | 1 Km |
| Medium Access | POLL |
| Max. node | 32 stations |
| Communication point | 32 points |

2.7 Communication Cable Specification

2.7.1 Profibus-DP Cable Specification

 Belden Network Cable

Type : Network Components

Protocol : FMS-DP-PA

Certification : No

Order No. : 3076F, 3077F, 3079A

| Classification | Twinax |  |
| --- | --- | --- |
| AWG | 22 |  |
| Type | BC-Bare Copper |  |
| Insulation | PE-Polyethylen |  |
| Insulation strength | 0.035 (Inch) |  |
| Shield | Aluminum Foil- Polyester Tape/Braid Shield |  |
| Capacitance | 8500㎊/ft |  |
| Characteristic impedance | 150Ω |  |
| Number of core wire | 2 Core |  |

2.7.2 DeviceNet Cable Specification

 Cable Specification

| Type name | Class 2 Thick/Thin Cable |  |
| --- | --- | --- |
| Maker | Allen-Bradley |  |
| Cable type | Round |  |
| Rated output voltage | 30V/100VA | Trunk/ drop |
| Max. allowable current | 100VA/24V or 4A | Simultaneous use |
| External diameter | 12.2mm/6.9mm |  |
| Number of core wire | 5 cores |  |

| Class 2 Thick Cable |  | Class 2 Thin Cable |
| --- | --- | --- |
| Spool Size |  | Spool Size |
| 50m |  | 50m |
| 150m |  | 150m |
| 300m |  | 300m |
| 500m |  | 600m |

 Cable Signal Name

Smart I/O Dnet I/F module cable have 5 cores as follows. It is composed of Twist pair cable for DC 24V power supply, twist pair cable for signal cable, shield cable etc. and both Thick and Thin cable are available for trunk/drop line.

| Cble color | Signal name | Description |
| --- | --- | --- |
| While | CAN_H | Signal cable |
| Blue | CAN_L | Signal cable |
| Bare | Drain | Shield cable |
| Black | V- | Power cable |
| Red | V+ | Power cable |

 Max. transmission distance by Cable types

| Transmission speed | Max. distance |  |
| --- | --- | --- |
|  | Thick cable | Thin cable |
| 125kbps | 500m | 100m |
| 250kbps | 250m | 100m |
| 500kbps | 100m | 100m |

<STRUCTURE>

Copper-film covered shield

Insulation covering

-Thick: Green

-Thin: Yellow

DC Power cable

-15AWG 19X28(Thick)

-22AWG 19X34(Thin)

Mylar Tape

Signal cable

(Blue/White)

-18AWG 19X30(Thick)

-24AWG 19X36(Thin)

Shielded cable

2.7.3 Rnet Cable Specification

 Twist Pair Cable

| Cable Description |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Product name |  | Low Capacitance Lan Interface Cable |  |  |  |
| Type name |  | LIREV-AMESB |  |  |  |
| Specification |  | 2*0.64 mm (GS 92-3032,22 AWG) |  |  |  |
| Maker |  | LG Cable |  |  |  |
| Electric characteristics |  |  |  |  |  |
| Items |  | Unit |  | Characteristics | Test condition |
| Conductor resistance |  | /km |  | Less than 59 | Normal temp. |
| Voltage-resistance(DC) |  | V/min |  | 500V 1 min resist | In air |
| Insulation resistance |  | MEGA -km |  | More than 1,000 | Normal temp. |
| Capacitance |  | pF/m |  | Less than 45 | 1 kHz |
| Characteristic impedance |  |  |  | 120  12 | 10MHz |
| Appearance characteristics |  |  |  |  |  |
| Conductor | No. of core wire |  | CORE | 2 |  |
|  | Spec. |  | AWG | 18 |  |
|  | Composition |  | NO./mm | 1/1.0 |  |
|  | Outside diameter |  | mm | 1.0 |  |
| Insulator | Thickness |  | mm | 0.9 |  |
|  | Outside diameter |  | mm | 2.8 |  |

Insulator

Conductor

● Structure Diagram

Grounding wire

2.7.4 Modbus Cable Specification

In case of Modbus communication using RS-422 channel, it is required to use Twist Pair Cable for RS-422 considering communication distance and communication speed. The table below shows the specification of recommended cable. In case of using other cables, it is required to use the cable suitable for the following characteristics.

 Product name : Low Capacitance Lan Interface Cable

 Type name   : LIREV-AMESB

 Spec.        : 2P X 22AWG(D/0.254 TA)

 Maker        : LG Cable

Twist Pair Cable Specification

| 1) Electric Characteristic |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Items |  | Unit |  | Characteristics | Test condition |
| Conductor resistance |  | /km |  | Less than 59 | Normal temp. |
| Voltage-resistance(DC) |  | V/1min |  | 500V 1 min resist | In air |
| Insulation resistance |  | M-km |  | More than 1,000 | Normal temp. |
| Capacitance |  | Pf/M |  | Less than 45 | 1kHz |
| Characteristics impedance |  |  |  | 120  12 | 10MHz |
| 2) Appearance Characteristic |  |  |  |  |  |
| Items |  |  |  | Single Wire |  |
| Conductor | No. of core wire |  | Pair | 2 |  |
|  | Spec. |  | AWG | 22 |  |
|  | Composition |  | NO./mm | 1/0.643 |  |
|  | Outside diameter |  | Mm | 0.643 |  |
| Insulator | Thickness |  | Mm | 0.59 |  |
|  | Outside diameter |  | Mm | 1.94 |  |

* Structure Diagram

Conductor

Insulator

Grounding wire

Braided material

Sheath material

2.8 Terminating

2.8.1 Profibus-DP Terminating

 Connection Connector

Terminal unit for cable

connection

A1 B1 A2 B2

A1 B1 A2 B2

OFF  ON

OFF  ON

Termination switch

ON : Terminating

OFF: no terminating

〈For end connection〉

〈For branch connection〉

2.8.2 DeviceNet Terminating

 Terminal resistance

- 121, 1%, 1/4W resistance should be added.

- Connected to CAN_H of connector and CAN_L signal cable

121 

Red

White

Black

Blue

Shield

| Remark |  |
| --- | --- |
| 1) Terminal resistance should be added to both end of trunk line of network and in case of composing by device port tab, it is required to install terminal resistance on both ends of tab. In case that terminal resistance is omitted, the normal communication is not available. |  |

2.8.3 Rnet Terminating

Signal cable for electric network connection for Smart I/O Rnet uses no.6 and 7 from connector pin of Rnet master module and no.8 and 9 of Smart I/O module.

No.6 signal of master module Is connected to no.8 signal cable of Smart I/O module and no.7 signal is connected to no.9 signal cable respectively.

As each connector body is connected to other module by shield cable which  plays the role to bypass the external noise, the connector bodies of both side should be connected by shield cable and the body of cable connector is not allowed to contact to high voltage and high current cables.

When soldering the shield cable to 9 pin connector body, it is required to heat the connector body with soldering iron sufficiently for strict and non removable soldering. In case of soldering, use the suitable amount of solder as too much solder adding makes the assembly of connector case difficult.

 Resistance value : 110, 1/2W

 Connection pin no.

- Master connection section : Pin no.6, 7

- Smart I/O connection section : Pin no.8, 9

 Terminal resistance as fittings(110, 1/2W) should be added on both ends of network.

 Connector case and end resistance are not allowed to contact each other.

Pin no.7

Pin no.6

Smart I/O connection

TX1 RX1 TX2 RX2

Terminal

resistance

End resistance

Master connection

Terminal unit for cable

connection

2.8.4 Modbus Terminating

In case of communicating through RS-422 channel, it should be required to connect the terminal resistance from outside. In case of long distance communication, terminal  resistance plays the role to prevent the signal distortion caused by reflection wave of cable and is required to connect the resistance (1/2W) same as characteristic impedance value to the end of network. In case of using the recommended cable, please connect 120 terminal resistance to both end of cable. In case of using other cables except the recommended cable, it is required to connect the 1/2W resistance same as the characteristic impedance value of using cable to both sides of cable.

Smart I/O connection

Terminal resistance

RX- RX+ TX- TX+

Master connection