# D. Siemens S5/S7 Series

## 1. S5/S7 Serial Interface

- Communication with Siemens S5/S7 Link Unit and PMU hardware using serial interface.

### 1-1.  System Configuration

(Using 3964R protocol)

| PLC | Interface Unit | Cable | Option Card | PMU |
| --- | --- | --- | --- | --- |
| S5 90U S5 95U S5 100U S5 115U S5 135U S5 155U S7-300 | CP525 CP340 | Refer to Cable Connection (RS-232C) | PMO-500/600S PMO-300S PMO-200S | PMU-500/600 PMU-300 PMU-200 |

### 1-2.  Cable Connection

(1)RS-232C connection(CP525 ↔ PMU series)

PLC part(25Pin)                                 PMU part(9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            FG

2            SD

3            RD

4           RTS

5           CTS

6           DSR

7            SG

8            CD

20          DTR

(2) RS-232C connection(CP340 ↔ PMU series)

PLC part(9Pin)                                 PMU part(9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            CD

3            SD

2            RD

7           RTS

8           CTS

6           DSR

5            SG

9            RI

4           DTR

### 1-3.  CP525/CP340 Setup

| PLC part setup |  |
| --- | --- |
| Baud rate | 110 bps ~ 19200 bps |
| Data length | 8 bit |
| Stop bit | 1 bit |
| Parity bit | EVEN |
| Error Detection | BCC(SUM) |

### 1-4.  PMU Setup

(1) Link Setup

- Select “Serial Link” in Link Editor and select “S5-3964R(Link)” in  “Siemens Series

- Setup the buffer No. of PMU with device of PLC

(Usable PLC address : Please refer to Chapter 10-2 address table

③ Transfer the link file to PMU with other files.

(2) Serial setup

Recommended setup as follows;

Baud rate : 19200 bps

Data length : 8bit

Stop bit length : 1bit

Parity bit: EVEN

Signal level : RS-232C

Station No. : None

## 1-5. PLC Address table

| Device | Word address |
| --- | --- |
| Input relay | IW000 ~ IW126 |
| Output relay | QW000 ~ QW126 |
| Internal relay | FW000 ~ FW254 |
| Timer | T000 ~ T255 |
| Counter | C000 ~ C255 |
| Data register *1 | D002:000 ~ D255:255 |
| Expanded Data register *1 | X002:000 ~ X255:255 |

Note

*1 : Data register and expanded Data register is described as follows D002:000 Data Word(DW) No. 000~255 Data Block(DB) No. 000~255 Expanded Data register is available for only S5 135U/155U.

## 2. S7-300 (Using MPI Port of CPU)

- Commincation with Siemens S7-300 through PC adapter and PMU hardware using serial interface

### 2-1.  System Configuration

| PLC | Interface Unit | Cable | Option Card | PMU |
| --- | --- | --- | --- | --- |
| CPU312IFM CPU313 CPU314 CPU315 CPU315-2DP | PC Adapter | Refer to cable connection (RS-232C) | PMO-500/600S PMO-300S PMO-200S | PMU-500/600 PMU-300 PMU-200 |

### 2-2.  Cable connection

(1)RS-232C connection(PC Adapter ↔ PMU series)

PLC part(9Pin)                                 PMU part(9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            CD

3            SD

2            RD

7           RTS

8           CTS

6           DSR

5            SG

9            RI

4           DTR

### 2-3.  S7-300 CPU Setup

| PLC part setup |  |
| --- | --- |
| Baud rate | 19200 ~ 38400 bps |
| Data length | 8 bit |
| Stop bit | 1 bit |
| Parity bit | ODD |
| Error Detection | BCC(SUM) |

### 2-4.  PMU Setup

(1) Link setup

- Select “Serial link” in Link Editor and select “S7-MPI(Loader)” in Siemens PLC

- Setup the buffer No. of PMU with device of PLC

(Usable PLC address : Please refer to Chapter 10-4 address table

③ Transfer the link file to PMU with other files.

(2) Serial Setup

Recommended setup as follows;

Baud rate : 38400 bps

Data length : 8bit

Stop bit length : 1bit

Parity bit : ODD

Signal level : RS-232C

Station No. : None

## 2-5.  PLC Address Table

| Device | Word address |
| --- | --- |
| Input relay | EW000 ~ EW126 |
| Output relay | AW000 ~ AW126 |
| Internal relay | MW000 ~ MW254 |
| Timer | T000 ~ T127 |
| Counter | Z000 ~ Z63 |
| Data register *1 | DB01.000 ~ DB60.65534 |

Note

*1 : Data register and expanded Data register is described as follows DB002.000 Data Word(DW) No. 000~65534 Data Block(DB) No. 01~60