# E. OMRON SYSMAC Series

## 1-1 OMRON SYSMAC-C Serial Interface

- Communication with OMRON SYSMAC-C PLC and PMU hardware using RS-232C/422

Serial Interface

### 1-1-1 System Cinfiguration

.

| PLC | Interface Module | Cable | Option Module | PMU |
| --- | --- | --- | --- | --- |
| C200H/C200HS | C200H-LK202-V1 | Below Drawing (RS-422) | PMO-500/600S PMO-300S PMO-200S | PMU-500/600 PMU-300 PMU-200 |
|  | C200H-LK201-V1 | Below Drawing (RS-232C) |  |  |
| C500/C1000H/ C2000H/C500 | C500-LK201-V1 C500-LK203 | Below Drawing (RS-232C/422) |  |  |
| C50/C120/C500/C1000H/C2000H/C120F/C500F | C120-LK201-V1 | Below Drawing (RS-232C) |  |  |
|  | C120-LK202-V1 | Below Drawing (RS-422) |  |  |

Note

Please be careful of Pin connection of Communication Unit for C200H/C200HS.(Refer to Cable Connection (2),(4))

### 1-1-2 Cable connection

(1) RS-232C connection(SYSMAC-C series ↔ PMU series)

All SYSMAC Series except C200.

PLC part(25Pin)                                  PMU part(9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            FG

2            SD

3            RD

4           RTS

5           CTS

6

7            SG

8            CD

20          DTR

(2) RS-232C connection(SYSMAC-C200 series ↔ PMU series)

For C-200 series.

PLC part(9Pin)                                 PMU part(9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            FG

2            SD

3            RD

4           RTS

5           CTS

6           +5V

7            DR

8            ER

9            SG

(3) RS-422 connection(SYSMAC-C Series ↔ PMU Series)

All SYSMAC-C Series except C200 Series

PLC Part(9Pin)                   PMU Part(6Pin or 5Pin Terminal Block)

1           RDA

2           RDB

3           SDA

4           SDB

5            SG

6            FG

1           RDA

2

3           SG

4

5           SDA

6           RDB

7            FG

8

9           SDB

(4)RS-422 Connection(SYSMAC-C200 Series ↔ PMU Series)

For C200 Series

PLC Part(9Pin)                   PMU Part(6Pin or 5Pin Terminal Block)

1           RDA

2           RDB

3           SDA

4           SDB

5            SG

6            FG

1           SDB

2           SDA

3           SG

4

5

6           RDB

7

8           RDA

9

### 1-1-3 SYSMAC-C PLC Setup

(1)C200H-LK201-V1/LK-202-V1 Setup

1) Station No. Setup

Station No. can be set by SW1 and SW2, SW1 means 10’s Digit, SW2 means

1’s digit value.

2) Baud rate Setup

Baud rate is setup by SW3. Set values of position of Switch are as

follows.

| Switch | Baud rate(bps) |
| --- | --- |
| 0 | 300 |
| 1 | 600 |
| 2 | 1200 |
| 3 | 2400 |
| 4 | 4800 |
| 5 | 9600 |
| 6 | 19200 |

3) commend level Setup

Commend level can be set by SW4. Position of recommended switch is SW2.

| Switch | Commend level | Parity | Others |
| --- | --- | --- | --- |
| 0 | Level 1 available | even | ASCII 7bit 2 Stop bit |
| 1 | Level 1, 2 available |  |  |
| 2 | Level 1,2,3 available |  |  |
| 3 | No setup level |  |  |
| 4 | Level 1 available | odd |  |
| 5 | Level 1,2 available |  |  |
| 6 | Level 1,2,3 available |  |  |
| 7 | No setup level |  |  |
| 8 | Level 1 available | even | JIS 8bit 1 Stop bit |
| 9 | Level 1,2 available |  |  |
| A | Level 1,2,3 available |  |  |
| B | No setup level |  |  |
| C | Level 1 available | odd |  |
| D | Level 1,2 available |  |  |
| E | Level 1,2,3 available |  |  |
| F | No setup level |  |  |

4) DIP Switch Setup

Note

Recommended Setup : CTS 0V(On), 1:N, Terminal Resistor “ Yes”.

(2)C500-LK201-V1 Dip Switch Setup

|  | Switch | Contents | Position of Set Switch |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ON |  |  |  |  |  |  | OFF |  |  |  |  |  |  |
| S W 1 | 1~5 | Station No. Select | 0 |  | 1 |  |  | 2 |  | … |  | 30 |  |  | 31 |  |
|  | 1 | Station No. Select | OFF |  | ON |  |  | OFF |  | … |  | OFF |  |  | ON |  |
|  | 2 |  | OFF |  | OFF |  |  | ON |  | … |  | ON |  |  | ON |  |
|  | 3 |  | OFF |  | OFF |  |  | OFF |  | … |  | ON |  |  | ON |  |
|  | 4 |  | OFF |  | OFF |  |  | OFF |  | … |  | ON |  |  | ON |  |
|  | 5 |  | OFF |  | OFF |  |  | OFF |  | … |  | ON |  |  | ON |  |
|  | 6 | Not used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | Not used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | PLC status when power”on” | Run |  |  |  |  |  |  | Stop |  |  |  |  |  |  |
| S W 2 | 1~4 | Baud rate select | 300 | 600 |  |  | 1200 |  | 2400 |  | 4800 |  | 9600 |  |  | 19200 |
|  | 1 | Switch select of Baud rate | OFF | ON |  |  | OFF |  | ON |  | OFF |  | ON |  |  | OFF |
|  | 2 |  | ON | OFF |  |  | OFF |  | ON |  | ON |  | OFF |  |  | OFF |
|  | 3 |  | OFF | OFF |  |  | OFF |  | ON |  | ON |  | ON |  |  | ON |
|  | 4 |  | ON | ON |  |  | ON |  | OFF |  | OFF |  | OFF |  |  | OFF |
|  | 5 | Not used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | Communication Method | 1:1 |  |  |  |  |  |  | 1:N |  |  |  |  |  |  |
|  | 7~8 | Available level setup | 1 |  |  | 1 |  |  |  | 1,2 |  |  |  | 1,2,3 |  |  |
|  | 7 | Command level setup | OFF |  |  | ON |  |  |  | OFF |  |  |  | ON |  |  |
|  | 8 |  | OFF |  |  | OFF |  |  |  | ON |  |  |  | ON |  |  |

Note Recommended Setup : Internal Synchronous, Terminal Resistor “Yes”, CTS(OV).

Note

Parity : Even, Data bit : 7bit, Stop bit : 2bit is fixed

3)C500-LK203 Dip Switch Setup

|  | Switch | Contents | Position of Setup Switch |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ON |  |  | OFF |  |  |
| S W 1 | 1~5 | Station No. Select | 0 | 1 | 2 | … | 30 | 31 |
|  | 1 | Station No. Select | OFF | ON | OFF | … | OFF | ON |
|  | 2 |  | OFF | OFF | ON | … | ON | ON |
|  | 3 |  | OFF | OFF | OFF | … | ON | ON |
|  | 4 |  | OFF | OFF | OFF | … | ON | ON |
|  | 5 |  | OFF | OFF | OFF | … | ON | ON |
|  | 6~7 | Parity & Transfer Code |  |  |  |  |  |  |
|  | 6 | Transfer Code | ASCII 7bt, 2 Stop bit |  |  | JIS 8bit, 1 Stop bit |  |  |
|  | 7 | Parity Setup | Even |  |  | Odd |  |  |
|  | 8 | PLC status when power “on” | Monitor |  |  |  |  |  |

|  | Switch | Contents | Position of Setup Switch |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ON |  |  |  |  | OFF |  |  |  |  |
| S W 2 | 1~4 | Baud rate Select | 300 | 600 |  | 1200 | 2400 |  | 4800 | 9600 |  | 19200 |
|  | 1 | Baud rate Select | OFF | ON |  | OFF | ON |  | OFF | ON |  | OFF |
|  | 2 |  | ON | OFF |  | OFF | ON |  | ON | OFF |  | OFF |
|  | 3 |  | OFF | OFF |  | OFF | ON |  | ON | ON |  | ON |
|  | 4 |  | ON | ON |  | ON | OFF |  | OFF | OFF |  | OFF |
|  | 5 | System Select | System #0 |  |  |  |  | System #1 |  |  |  |  |
|  | 6 | Communication Method | 1:1 |  |  |  |  | 1:N |  |  |  |  |
|  | 7~8 | Available command Level | 1 |  | 1 |  |  | 1,2 |  |  | 1,2,3 |  |
|  | 7 | Command level Select | OFF |  | ON |  |  | OFF |  |  | ON |  |
|  | 8 |  | OFF |  | OFF |  |  | ON |  |  | ON |  |

Note Recommend setup : Internal Synchronous, Terminal Resistor “Yes”, CTS(OV).

(4)C120-LK201-V1/LK-202-V1 Setup

|  | Switch | Contents | Position of Setup Switch |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ON |  |  |  |  |  |  | OFF |  |  |  |  |  |  |
| S W 1 | 1~5 | Station No. Select | 0 |  | 1 |  |  | 2 |  | … |  | 30 |  |  | 31 |  |
|  | 1 | Station No. Select | OFF |  | ON |  |  | OFF |  | … |  | OFF |  |  | ON |  |
|  | 2 |  | OFF |  | OFF |  |  | ON |  | … |  | ON |  |  | ON |  |
|  | 3 |  | OFF |  | OFF |  |  | OFF |  | … |  | ON |  |  | ON |  |
|  | 4 |  | OFF |  | OFF |  |  | OFF |  | … |  | ON |  |  | ON |  |
|  | 5 |  | OFF |  | OFF |  |  | OFF |  | … |  | ON |  |  | ON |  |
|  | 6 | Not used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | Not used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | PLC status when power “on” | Run |  |  |  |  |  |  | Stop |  |  |  |  |  |  |
| S W 2 | 1~4 | Baud rate Select | 300 | 600 |  |  | 1200 |  | 2400 |  | 4800 |  | 9600 |  |  | 19200 |
|  | 1 | Baud rate Select | OFF | ON |  |  | OFF |  | ON |  | OFF |  | ON |  |  | OFF |
|  | 2 |  | ON | OFF |  |  | OFF |  | ON |  | ON |  | OFF |  |  | OFF |
|  | 3 |  | OFF | OFF |  |  | OFF |  | ON |  | ON |  | ON |  |  | ON |
|  | 4 |  | ON | ON |  |  | ON |  | OFF |  | OFF |  | OFF |  |  | OFF |
|  | 5 | Not used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | Communication Method | 1:1 |  |  |  |  |  |  | 1:N |  |  |  |  |  |  |
|  | 7~8 | Available command level | 1 |  |  | 1 |  |  |  | 1,2 |  |  |  | 1,2,3 |  |  |
|  | 7 | Command level Select | OFF |  |  | ON |  |  |  | OFF |  |  |  | ON |  |  |
|  | 8 |  | OFF |  |  | OFF |  |  |  | ON |  |  |  | ON |  |  |

①C120-LK201-V1

|  | Switch | Contents | Position of Setup Switch |  |
| --- | --- | --- | --- | --- |
|  | 1~2 | CTS Select | CTS Nomal ON | Using External CTS |
|  | 1 |  | ON | OFF |
|  | 2 |  | OFF | ON |
|  | 3~6 | Select of Synchronous | Internal Synchronous | External Synchronous |
|  | 3 |  | ON | OFF |
|  | 4 |  | OFF | ON |
|  | 5 |  | ON | OFF |
|  | 6 |  | OFF | ON |
|  | 7 | Not used |  |  |
|  | 8 | Not used |  |  |

②C120-LK202-V1

|  | Switch | Contents | 설정 스위치 상태 |  |
| --- | --- | --- | --- | --- |
|  | 1~2 | Select of Terminal Resistor | Yes | No |
|  | 1 |  | ON | ON |
|  | 2 |  | OFF | OFF |
|  | 3 |  | ON | OFF |
|  | 4 |  | OFF | OFF |
|  | 5 |  | ON | OFF |
|  | 6 |  | OFF | OFF |
|  | 7 | Not used |  |  |
|  | 8 | Not used |  |  |

Note

Recommended Setup : Internal Synchronous, Terminal Resistor “ Yes”, CTS (O).

Caustionn

In communication, PLC mode should be “Monitor” Mode. If not, Writing in PLC is not allowed.

(5)C200HW-COM06 Setup

Setup for OMRON C200 PLC

Setup is don by internal memory of PLC. (Please refer to PLC Manual)

If do not set, Basic setup is  RS232C, 9600, 7bit, 2bit, even.

Caution

In communication, PLC mode should be “Monitor” Mode. If not, Writing in PLC is not allowed.

RS-422 communication when using communication module

The following switch is installed on C200HW-COM06.

RS422/RS485 2 Wire system

SW1  : 2 Setting  	SW2  : 1 Setting

RS422/RS485 4 Wire system

SW1  : 4 Setting	        SW2  : ON Setting

When communication with PMU and RS-422 module, please use set 4 Wire system.

(Set ofRS-422, please refer to PLC Manual)

### 1-1-4 PMU Setup

### (1) Link Setup

- Select “Serial Link” in the Link Editor, set “SYSMAC-C(Link)” in OMRON

PLC.

② Set buffer which is related with PLC address in Link Editor. Please refer to Chapter 5-3 for available PLC address.

③ Download the Link information to PMU.

(2) Serial Setup

Serial setup should ne don as follows;

Baud rate : The same as PLC sets.

Data lentgth : The same as PLC sets.

Stop bit length : The same as PLC sets.

Parity bit : The same as PLC sets.

Signal level : The same as PLC sets.

PMU station No. : The same as PLC sets.

## 1-2 Available Address Table

(1)공통

| Dev | In writing | 50,120(F),500(F) | 2000H, 200H(S), 1000H(F) |
| --- | --- | --- | --- |
| LR | LR | 0~31 | 0~63 |
| HR | HR | 0~31 | 0~99 |
| TIM | TIM | 0~127 | 0~511 |
| CNT | CNT | 0~127 | 0~511 |
| DM | DM | Please refer to below DM(Data Memory)table. |  |
| AR | AR | None | 0~27 |
| I/O | CH | 0~63 | 0~255 (0~511:200HS) |

(2)DM Area

| C50,120,500 | 0~511 |
| --- | --- |
| C200H | 0~1999 |
| C200HS | 0~9999 |
| 1000H | 0~4096 |
| 2000H | 0~6655 |
| 120F | 0~511 |
| 500F | 0~4095 |
| 1000HF | 0~4095 |

* Bit ON/OFF can be done in only LR,HR,AR,CH.