# 5. Samsung FARA Series

## 5-1 FARA-N PLC Serial Interface

Communication between PMU and Samsung FARA-N PLC through  RS-232C/422 .

### 5-1-1 System Configuration

System configuration of PMU and Samsung FARA-N PLC

| PLC | Interface Unit | Cable | Interface Card | PMU |
| --- | --- | --- | --- | --- |
| FARA-N | N-7000 CCU N-700 CCU | Refer to Cable connection (RS-232C) | PMO-500/600S PMO-300S PMO-200S | PMU-500/600 PMU-300 PMU-200 |

### 5-1-2 Cable connection

(1)RS-232C Connection(FARA Series ↔ PMU)

PLC (9Pin)                                     PMU (9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            FG

2            SD

3            RD

4           RTS

5           CTS

6

7            SG

8            CD

9           DTR

### 5-1-3 FARA PLC Set up

Please find Dip S/W Setting of FARA PLC which is located in the rear sid eof communication Unit. It is only possible to Communication with PMUPMU through

RS-232C, and baud Rate is 300~19200bps.

| Switch | Setting | Status of Switch Set |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ON |  |  |  |  | OFF |  |  |  |
|  | Baud Rate(bps) | 300 | 600 | 1200 | 2400 | 4800 |  | 9600 | 19200 | Modem |
| SW1 | Baud Rate Setting | ON | OFF | ON | OFF | ON |  | OFF | ON | OFF |
| SW2 |  | ON | ON | OFF | OFF | ON |  | ON | OFF | OFF |
| SW3 |  | ON | ON | ON | ON | OFF |  | OFF | OFF | OFF |
| SW4 | Data Bit | 8 Bit |  |  |  | 7 Bit |  |  |  |  |
| SW5 | Parity Yes/No | Yes |  |  |  | No |  |  |  |  |
| SW6 | Even/Odd Parity | Even |  |  |  | Odd |  |  |  |  |
| SW7 | Stop Bit 설정 | 2 Bit |  |  |  | 1 Bit |  |  |  |  |
| SW8 | Control Signal | CTS,CD available |  |  |  | CTS,CD not available |  |  |  |  |

Please set SW8 (Control Signal) as OFF(CTS,CD not available).

### 5-1-4 PMU Set-up

(1) Link Se-up

- Please select “Serial Link” in the Link Editor and select “ FARA-N(Link) in the

FARA PLC Series.

- Please set buffer which will be linked with PLC Address.

Please refer to Available PLC Address in Chepter 5-3..

③ Please transfer Link information to PMU.

(2) Serial Set-up

Please set the serial data as follows;.

Baud Rate    : Same as PLC Set-up.

Data Length   : Same as PLC Set-up.

Stop Bit Length : Same as PLC Set-up.

Parity Bit      : Same as PLC Set-up.

Signal Level   : Same as PLC Set-up.

PMU Station Number : Same as PLC Set-up.

## 5-2 FARA-N PLC CPU Communication(Loader Port)

Communication between PMU and FARA-N PLC through Loader Port.

### 5-2-1 System Configuration

Communication through FARA-N PLC through Loader Port.

| PLC | Interface Unit | Cable | PMU Interface | PMU |
| --- | --- | --- | --- | --- |
| FARA-N | None | Referer to cable connection (RS-232C) | PMO-500/600S PMO-300S PMO-200S | PMU-500/600 PMU-300 PMU-200 |

### 5-2-2 Cable connection

(1)RS-232C connection(FARA Series(Loader Port) ↔ PMU )

PLC (15Pin)                                    PMU (9Pin)

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            FG

6            RD

7            SG

13           SD

### 5-2-3 FARA-N PLC Set-up

No need to set any FARA-N PLC data

### 5-2-4 PMU Set-up

### (1) Link Set-up

- ①Please select “Serial Link” in the Link Editor and select “ FARA-N(Loader) in the

FARA PLC Series.

.

② Please set buffer which will be linked with PLC Address.

Please refer to Available PLC Address in Chepter 5-3..

③ Please transfer Link information to PMU

(2) Serial Set-up

No need to set-up any data, the followings will be set-up automatically.

Baud Rate : 9600 bps/19200 bps (Selectable)

Data Length : 8bit

Stop Bit Length : 1bit

Parity Bit : Odd

Signal Level : RS-232C

PMU Station No. : “ 0” Station

## 5-3 Available PLC Address

| Operand | Name | Data | Points | Address |
| --- | --- | --- | --- | --- |
| X | External Input Relay | Bit | 2048 | 0 ~ 127F *1 |
| Y | External Output Relay | Bit | 2048 | 0 ~ 127F *1 |
| R | Internal Relay | Bit | 1568 | 0 ~ 97F *1 |
| L | Link Relay | Bit | 2048 | 0 ~ 127F *1 |
| R | Special Relay | Bit | 176 | 9000 ~ 910F *1 |
| T/C | Timer/Counter Contact | Bit | 256 | 0~255 |
| DT | Data Register | Word | 2048 | 0 ~2047 |
| FL | File Register | Word | 22525 | 0 ~ 22524 |
| Ld | Link Register | Word | 256 | 0 ~ 255 |
| DT | Special Rrgister | Word | 256 | 9000 ~ 9255 |
| SV | Timer/Counter Setting Area | Word | 256 | 0 ~ 255 |
| EV | Timer/Counter Current Area | Word | 256 | 0 ~ 255 |
| IX/IY | Index Register | Word | 2 | IX/IY |

참고

*1 : X,Y,R,L can be implemented both Bit and Word. In case of Bit implementation, 1 Digit will be Hexa, 10 Digit should be Decimal. (Example : X12C) In case of Word implementation, please put “W” in fornt of data. (Example : WX12 = 16 Bit Data of X120~X12F)