Appendix. Getting Started

- Edit a Main Screen	A-2

1-1. Create a Main Screen 	A-2

1-1-1. Create a Function Key Tag	A-3

1-1-2. Create a Numeric Tag	A-6

1-1-3. Create a Lamp Tag	A-8

1-2. Simulation 	A-10

A. GE-Fanuc 90-30[SNP-X] Series

1. Edit a Link Editor	A-13

2. Edit a Project Manager	A-15

3. Setup a PMU hardware	A-17

4. Edit a Program in PLC 	A-20

5. Cable Connection for serial Interface	A-21

B. Allen-Bradley PLC Series

1. SLC500 PLC CPU Connection	A-22

1-1. System Configuration	A-22

1-2. Cable Connection	A-22

1-3. SLC500 PLC Setup	A-22

1-4. PMU Setup	A-23

2. PLC-5 Connection	A-24

2-1. System Configuration	A-24

2-2. Cable Connection	A-25

2-3. PLC-5 PLC Setup	A-25

2-4. PMU Setup	A-25

3. PLC Address	A-27

- Edit a main screen

1-1. Create a main screen

When you install PMU-MASTER software, 6 kinds of file managers will be created in Program group of Start menu.

- Select Project Manager in the PMU-MASTER Program group.

- Select PMU type and click OK button.

(You can select PMU type later by selecting File - Change PMU Type menu in the Project Manager)

①

②

- Select Editor-Screen Editor in the full down menu to create a drawing file.

1-1-1. Create a Function Key Tag

- Select Text menu in Draw menu or Text tool (    ) to insert text.

Insert text after clicking a mouse.

①

②

- Select Tag Insert-Function Key in the full down menu.

- Place the direction icon of the function key tag on the main screen and click a mouse.(Position does not matter)

Then, Function Key Tag dialog box appears.

- After entering a name of the Function Key Tag, select function key.

- Click Bit button(You can select Bit, Word or Special button)

※ Tag Name : The initial letter begins as ‘F’ and you can enter the name up to 5 characters(English, Numeric

number) including initial letter.

- Enter buffer number and bit position of selected buffer. Then select operation method.

※ User defined buffer number begins from 40(to 1024). (Please refer to User’s Manual – [Appendix A-3])

This buffer number should be matched with PLC memory address. To communicate with PLC, you need to

setup the Link Editor in the Project manager.

- Click OK button.

1-1-2. Create a Numeric Tag

This tag indicates the value of the system’s buffer data at the actual time on the screen of the main machine.

- Select Tag Insert-Numeric in the full down menu.

- Move a cursor to the place to be created and click a left mouse button.

- Enter the Tag Name and define a buffer address(from 40 to 1024: Be sure not to overwrite the buffer address with other tags)

- When it is in Decimal, it indicates a maximum of 10 digits and when it is in BCD or HEX, it indicates a maximum of 8 digits.  The two methods of indicating the data are by absolute value and in relative value.

- When the indication method is of relative value, and the specified buffer data goes beyond the top inch and bottom inch, it will flicker.

- You can determine the indicated data’s decimal point position.

- Select Data Form as Absolute type, Data Type as Signed DEC16bit, Indication digit as ‘5’ and Decimal point as ‘0’.

- After setting up the configuration, click OK button.

If you enter the data ‘-12345’ in buffer 41, the numeric tag will be displayed in the simulation or run mode as below.

If the data type is Signed Decimal 16bit or Signed Decimal 32bit, the total indication place is actually one place more than the Digit number.

-12345678

- Example)  Data type: Signed DEC 16bit,  Digit Number: 8

- By double clicking the tag to edit on the editor screen, you can edit the already created tag.

[Note]

To move a tag, select this icon.

To copy a tag, select this icon.

To cut(delete) a tag, select this icon.

1-1-3. Create a Lamp Tag

According to the condition of the specified bit in the specified buffer, the specified color changes by the lamp.

- Select Circle icon on the toolbox to draw a circle.

- Draw a circle by dragging a mouse with pressing a left button.

- After selecting the territory to be drawn, drop the mouse button.

- Select Tag Insert-Lamp in the full down menu.

- Move a mouse on the circle(center of circle) and click the left button.

- Select Lamp Type(Select ‘Painted Circle’), Condition.

- Click OK button.

- Draw the lamp area the same size as circle.

1-2. Simulation

You can simulate the edited screen in the computer before you download this file to PMU main machine.

You should save the created screen as a file before the simulation.

The name of the main screen should be saved as number from 1 to 999.

To confirm the contents of file, It’s better to describe the contents in the description box.

* For the main screen, the file type should be saved as *.scr.

from 1 to 999

- Select Others-Simulation in the full down menu.

- If you want to insert an alarm file or message file, select the files in the list box.

- Click OK button.

- You can simulate the main screen by using the simulation tool kit (Enter Tool) or Function Keys.

- Enter the buffer number to be simulated and the value in the Enter Tool dialog box.

- Press Enter Key to enter the data.

If you press the function key ‘F1’ with the mouse, the key will be activated. The value of the buffer will be changed into ‘1’.

The Status

 ‘ON’,

Momentary

Operation

The status of the designated bit

(If you setup the bit number as

‘3’ the data of the buffer(40) will be

0000-0000-0000-1000)

If you select the type of the touch tag as

# Word, these 16 bits will be displayed as

Data value.

- You can find that the lamp is ‘ON’ when you press function key ‘F1’ button.

[Note]

Please notice the types of the tags. In the above simulation, the data of the Lamp Tag or the Numeric Tag except Touch Tag should be sent from PLC(that is, Reading data from PLC). While, the data of the Touch Tag should be sent from PMU(that is, Writing data to PLC). This notice is very important to setup the link editor for the communication between PLC and PMU.

- You can view the list of the buffers created in the main screen.

- To finish the simulation, select the Simulation Exit in the full down menu.

A. GE-Fanuc 90-30[SNP-X] series

1. Edit a Link Editor

For the communication with PLC when operating the main machine (PMU), the Link Editor allows you to enter and select the communication method, PLC Type, Device, Address and others in the Link Table.

To use the selected Link File, Send a Link File from PC to the main machine (PMU) using Project Manager.

The extension name for the Link Select File is “.LNK”.

- Select Others-Link Editor in the Screen Editor or Editor-Link Editor in the Project Manager.

Select SERIAL Link button to setup the serial communication.

①

②

③

- Select PLC Series and Link type, then click OK button.

- Enter the PLC address for the communication.

When you set a PLC address on the buffer memory area, be sure that the buffer memory is a word data.

So, M0001, R0001 are word data.

Buffer no. 40 : Function Key Tag and Lamp Tag(Writing data to PLC) – Bit data(ex. M0001 card)

Buffer no. 41 : Numeric Tag(Reading from PLC) - Word data(ex. R001 card)

- Click OK button.

- Select File – Save menu

- Select folder to be saved and enter file name, then click OK button.

- Edit a Project Manager

- Select Others-Project Manager in the Screen Editor or Open the Project Manager in PMU-MASTER.

- Select Make project file button and click OK button.

- Click OK button after setting up the directory.

- Double click on the file to insert the file into a project file to be created.

- Then the selected file will be moved to the right box as the above.

- Select Make PRJ button.

- Enter file name of the project file, then click OK button.

- Select Communication-Send Project File in the Project Manager.

- Press Start button to send PRJ file to PMU hardware after setting up the PMU hardware for the communication.

- Setup a PMU hardware

To communicate with PLC, you should download the Project file[*.scr, *.sub, *.alm, *.lnk, *.msg and etc.] created in the PMU-MASTER to the PMU hardware.

To setup the PMU hardware(main unit),

- Turn the power On[the power supply for the PMU-200 is DC24V].

Press a function key ‘F3’’ in the Main Menu of the main unit.

P M U – 2 0 0

Self Test

<F1>

Initial Setup

<F2>

Transfer

<F3>

Run

<F4>

Press function key ‘F1’ to be ready.

- Transfer the files from the Project Manager of the PMU-MASTER. to the Main Unit.

- Press Start button.

- The message “ Receiving…” appears during the downloading in the Main Unit.

- ‘Completed! <KEY>’ message is shown to the main unit after execution.

- To interrupt transfer, press ESC key. (Function key ‘MENU’ in the machine)

- Before the communication, you should set the Initial Setup in the Main Menu.

- Press Initial Setup key and select Serial Setup key.

- Setup value is :

Baud rate : 19200bps

Data bits : 8bits

Stop bit : 1bit

Parity bit : odd

Interface : RS-422(4line)

Station number : 0

To select the left menu bar(Items) : Use Function key ‘∧’ and ‘∨’.

Baud rate

Data bits

Stop bits

Parity bit

Station Number

Interface

Save<ENTER>

Cancel<MENU>

:

:

:

:

:

:

[ 19200]

7bits     8bits

1bit      2bits

None  Even   Odd

[ 0]

RS232     RS422

- To select the parameter : Use Function key ‘＜’ and ‘＞’.

- To escape the current screen, press Cancel button.

- Press Enter button.

- Edit a Program in PLC

To communicate with PMU and PLC, you should download a program to PLC using Programming

Tool(LOGICMASTER 90 Software)

- Create a Program for the communication.

M0001 : Bit address for Touch Tag and Lamp Tag( Buffer : 40, Bit number : 0)

R0001 : Word address for Numeric Tag(Buffer : 41. Word data)

- For the detail information of editing a program in the programming tool, please refer to the User’s Manual.

5. Cable Connection for serial Interface

9 pin            9 pin

2                2

3                3

5                5

[Male]          [Female]

PMU + Serial Option card

PC

4 pin            15 pin

RDA              13

RDB              12

SDA	         11

SDB              10

9

6

15

8

14

PMU          PLC[Male]

GE Fanuc(90-30)series- Loader Port

B. Allen-Bradley PLC series

## 1. SLC500 PLC CPU Connection

- Allen-Bradley :SLC500 PLC – PMU RS-232C interface using Loader port

### System configuration

SLC500 PLC – PMU hardware

| PLC | Interface module | Cable | Option unit | PMU |
| --- | --- | --- | --- | --- |
| SLC5/03 SLC5/04 | None | Below drawing (RS-232C) | PMO-600S PMO-300S PMO-200S | PMU-600 PMU-300 PMU-200 |

### Cable connection

- RS-232C connection(SLC500 series ↔ PMU series)

PLC part(9Pin)                                    PMU part(9Pin)

1            CD

2            RD

3            SD

4          DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            CD

2            RD

3            SD

4          DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1-3 SLC500 PLC setup

recommend: 19200 bps, data: 8 bit, stop bit:1 bit, parity: Even

| Setup of PLC part |  |
| --- | --- |
| Baud rate | 19200 bps |
| Data length | 8 bit |
| Stop bit | 1 bit |
| Parity bit | EVEN |
| Communication Driver | DF1 Half Duplex Slave |
| Duplicate Packet Detection | Disable |
| Error Detection | BCC |
| Control Line | No Handshaking |
| Station Address | 0 |

Please remember station Address of PLC and the station number of PMU should be identified.

### 1-4 PMU setup

(1) Link setup

- select serial link in link editor and select “SLC500[5/03,04](LOADER)” in AB series.

② setup the buffer no. of PMU with device of PLC

(PLC address : please refer to the address table)

③Transfer the link file to PMU with other files.

(2)Serial setup

It should be identified with PLC data.

## 2. PLC-5 PLC CPU connection

Allen-Bradley :SLC5 PLC - RS-232C interface using Loader port

### 2-1. System configuration

| PLC | Interface module | cable | Option card | PMU |
| --- | --- | --- | --- | --- |
| PLC-5/11 PLC-5/20 PLC-5/30 PLC-5/40 PLC-5/40L PLC-5/60 PLC-5/60L | None | Below drawing (RS-232C, RS-422) | PMO-600S PMO-300S PMO-200S | PMU-600 PMU-300 PMU-200 |

### 2-2. Cable connection

(1)RS-232C connection (PLC-5 series ↔ PMU series)

PLC part(25Pin)                                      PMU part(9Pin)

1           RDA

2           RDB

3           SDA

4           SDB

5            SG

6            FG

1            FG

2           SDA

3           RDA

4

5

6

7

14          SDB

16          RDB

1            CD

2            RD

3            SD

4           DTR

5            SG

6           DSR

7           RTS

8           CTS

9

1            FG

2            SD

3            RD

4           RTS

5           CTS

6           DSR

7            SG

8            CD

20          DTR

(2)RS-422 connection (PLC-5 series ↔ PMU series)

PLC part(25Pin)             	     PMU part(6Pin or 5Pin Terminal Block)

### 2-3 PLC-5 PLC setup

recommend: 19200 bps, data: 8 bit, stop bit:1 bit, parity bit: Even.

| PLC part |  |
| --- | --- |
| Baud rate | 19200 bps |
| Data length | 8 bit |
| Stop bit | 1 bit |
| Parity bit | EVEN |
| Communication Driver | DF1 Half Duplex Slave |
| Duplicate Packet Detection | Disable |
| Error Detection | BCC |
| Control Line | No Handshaking |
| Station Address | 0 |

Please remember station address of PLC and the station number of PMU should be identified.

### 2-4 PMU setup

(1)Link setup

①select serial link in link editor and select “SLC5(LOADER)” in AB series.

② setup the buffer no. of PMU with device of PLC

(PLC address : please refer to the address table)

③Transfer the link file to PMU with other files.

(2) Serial Setup

It should be identified with PLC data.

## 3. PLC Address

(1)SLC500 series

| Device | Address |
| --- | --- |
| Bit | B003000 ~ B003255 , B010000 ~ B255255 |
| Timer (Timing bit) *1 | TC004000 ~ TC004255 , TC010000 ~ TC255255 |
| Timer (complete bit) *1 | TC004000 ~ TC004255 , TC010000 ~ TC255255 |
| Timer (setting value) | TP004000 ~ TP004255 , TP010000 ~ TP255255 |
| Timer (current value) | TA004000 ~ TA004255 , TA010000 ~ TA255255 |
| Counter (Up counter) *2 | CC005000 ~ CC005255 , CC010000 ~ CC255255 |
| Counter (down counter) *2 | CC005000 ~ CC005255 , CC010000 ~ CC255255 |
| Counter (complete bit) *2 | CC005000 ~ CC005255 , CC010000 ~ CC255255 |
| Counter (setting value) | CP005000 ~ CP005255 , CP010000 ~ CP255255 |
| Counter(current value) | CA005000 ~ CA005255 , CA010000 ~ CA255255 |
| Integer | N007000 ~ N007255 , N010000 ~ N255255 |

Note

*1 : Timing bit : bit 14 complete bit : bit 13 *2 : Up counter Enable bit : bit 15 Down counter timing bit : bit 14 Complete bit : bit 13

(2)PLC-5 series

| Device | Address |
| --- | --- |
| Input relay | I001000 ~ I001999 |
| Output relay | O000000 ~ O000999 |
| Internal relay | B003000 ~ B099999 |
| Timer(Timing bit) *1 | TC003000 ~ TC099999 |
| Timer(Complete bit) *1 | TC003000 ~ TC099999 |
| Timer(Setting value) | TP003000 ~ TP099999 |
| Timer(current value) | TA003000 ~ TA099999 |
| Counter (Up counter) *2 | CC003000 ~ CC099999 |
| Counter (down counter) *2 | CC003000 ~ CC099999 |
| Counter (complete bit) *2 | CC003000 ~ CC099999 |
| Counter (setting value) | CP003000 ~ CP099999 |
| Counter (current value) | CA003000 ~ CA099999 |
| Integer | N003000 ~ N099999 |

Note

*1 : Timing bit : bit 14 Complete bit : bit 13 *2 : Up counter Enable bit : bit 15 complete bit : bit 13