## F. PMU Communication  With Mitsubishi PLC CPU(Loader Port)

This is for communicating between PMU _ Mitsubishi PLC Loader Port

### 1-1 System Configuration

| PLC | Communication Unit | Cable | Communication Module for PMU | PMU |
| --- | --- | --- | --- | --- |
| M2N,M3N | None | PMC-422C | PMO-600S PMO-300S PMO-200S | PMU-600 PMU-300 PMU-200 |
| M2A,M3A |  |  |  |  |
| M2U,M3U |  |  |  |  |
| A1S,A2S |  |  |  |  |
| M0J2,AOJ2H |  |  |  |  |
| QnA |  |  |  |  |
| FX |  |  |  |  |

### 1-2  Cable Connection

### (1)RS-232C Connection (Melsec Series ↔ PMU )

### 1-3 Melsec PLC Set up

You don’t need to set any data for Melsec PLC.

### 1-4 PMU Set up

- Link Set up

- Please select Interface Type(“Serial”) first and then select PLC Type as follows;(“A2N,A3N(LOADER)”, “A2A,A3A(LOADER)”, “A2U,A3U(LOADER)”, “AnS,AOJ2H(LOADER)”, “A0J2(LOADER)”, “QnA(LOADER)”,”FX”)

① Please set up buffer memory which will be linked with PLC address.

- Please refer to Table      for Available PLC Address.

- Transfer Information(Link) to PMU.

(2) serial Set up

You don’t need to set up anything, Data will be set up automatically as follows.

Baud Rate : 9600 bps

Data Length : 8bit

Stop Bit Length : 1bit

Parity Bit : Even

Signal Level : RS-232C

Station No. : 0

## Table 2-1 Available PLC Address Table

- AnU CPU (Loader Port Communication)

| Contents | Dev.No | Data | Registerd Bit Address | Registered Word Address |
| --- | --- | --- | --- | --- |
| Input (X) | 0 | Bit | X0000 – X1FFF |  |
| Output (Y) | 1 | Bit | Y0000 – Y1FFF |  |
| LINK Relay (B) | 2 | Bit | B0000 – B1FFF |  |
| LINK Register (W) | 3 | Word |  | W0000 – W1FFF |
| STEP Relay (S) | 4 | Bit | S0000 - S8191 |  |
| Special Relay (F) | 5 | Bit | F0000 – F2047 |  |
| LATCH Relay (L) | 6 | Bit | L0000 – L8191 |  |
| Internal Relay (M) | 7 | Bit | M0000 – M8191 |  |
| Special Relay (M) | 7 | Bit | M9000 - M9255 |  |
| Data Register (D) | 8 | Word |  | D0000 - D8191 |
| Special Register (D) | 8 | Word |  | D9000 - D9255 |
| Timer-Coli (TC) | 9 | Bit | TC000 – TC2047 |  |
| Timer-Current (TN) | 10 | Word |  | TN000 – TN2047 |
| Timer-Contact (TS) | 11 | Bit | TS000 – TS2047 |  |
| Counter-Coil (CC) | 12 | Bit | CC000 – CC1023 |  |
| Counter-Current (CN) | 13 | Word |  | CN000 – CN1023 |
| Counter-Contact (CS) | 14 | Bit | CS000 – CS1023 |  |

(2) QnA CPU (Loader Port Communication)

| Contents | Dev.No | Data | Registerd Bit Address | Registered Word Address |
| --- | --- | --- | --- | --- |
| Input (X) | 0 | Bit | X0000 – X1FFF |  |
| Output (Y) | 1 | Bit | Y0000 – Y1FFF |  |
| Link Relay (B) | 2 | Bit | B0000 – B7FFF |  |
| Link Register (W) | 3 | Word |  | W0000 – W63FF |
| Special Link Register (SW) | 3 | Word |  | SW000 – SW7FF |
| Step Relay (S) | 4 | Bit | S00000 - S32767 |  |
| Special Relay (F) | 5 | Bit | F00000 – F32767 |  |
| Latch Relay (L) | 6 | Bit | L00000 – L32767 |  |
| Edge Relay (V) | - | Bit | V00000 - V32767 |  |
| Internal Relay (M) | 7 | Bit | M00000 – M32767 |  |
| Special Relay (SM) | 7 | Bit | SM0000 – SM2047 |  |
| Data Register (D) | 8 | Word |  | D00000 – D25599 |
| Special Register (SD) | 8 | Word |  | SD0000 – SD2047 |
| Timer-Coil (TC) | 9 | Bit | TC0000 – TC23551 |  |
| Timer-Current (TN) | 10 | Word |  | TN0000 – TN23551 |
| Timer-Contact (TS) | 11 | Bit | TS0000 – TS23551 |  |
| Acummulating Timer-Coil (SC) | - | Bit | SC0000 – SC23551 |  |
| Acummulating Timer-Current (SN) | - | Word |  | SN0000 – SN23551 |
| Acummulating Timer-Contact (SS) | - | Bit | SS0000 – SS23551 |  |
| Counter-Coil (CC) | 12 | Bit | CC0000 – CC23551 |  |
| Counter-Current (CN) | 13 | Word |  | CN0000 – CN23551 |
| Counter-Contact (CS) | 14 | Bit | CS0000 – CS23551 |  |

(3) MELSEC-FX Series CPU (Loader Port Communication)

| Contents | Dev.No | Data | Registerd Bit Address | Registered Word Address |
| --- | --- | --- | --- | --- |
| Input (X) | 0 | Bit | X000 – X337 | X000 – X320 |
| Output (Y) | 1 | Bit | Y000 – Y337 | Y000 – Y320 |
| Step Relay (S) | 2 | Bit | S000 – S999 | S000 – S984 |
| Internal Relay (M) | 3 | Bit | M0000 – M1535 | M0000 – M1520 |
| Data Register (D) | 4 | Word |  | D000 – D999 |
| Timer-현재치 (TN) | 5 | Word |  | TN000 – TN255 |
| Counter-Current (CN) | 6 | Word |  | CN000 - CN255 |