# Chapter 9. Troubleshooting

At this chapter, description and actions taken for various errors occurring with positioning module are explained. Occurring errors are largely divided into the non-critical and the critical.

Error occurrence is indicated by LED on the top of product and an error type may be checked with Teaching unit (G0F-PTUA) and software package (Position.exe).

## 9.1 Error type and correction

[Positioning module error code table]

| Error code | Description |
| --- | --- |
| 0 | Normal operation |
| 1 | Base positioning number exceeding setting range. |
| 2 | H/W error of base |
| 3 | Slot positioning number exceeding setting range. |
| 4 | Slot not mounted |
| 5 | Module name different |
| 6 | Axis range exceeding setting range. |
| 7 | CPU module gives out a control during Stop condition. |
| 8 | Common RAM error |
| 9 | FB control can not be executed since module is in operation/stop condition. |
| 10 | A function block of a new control is REQ before a previous control is completed. |
| 11 | Setting value of auxiliary input exceeding the range. |
| 13 | Stop-related controls or emergency stop is entered during the execution of function block. |
| 14 | NM or OR control is entered when not in normal speed phase of automatic operation. |
| 15 | A control issued when module zeroing is not complete. (Teaching) |
| 17 | H/W error |
| 18 | Watchdog time error |
| 19 | Interface with CPU error |
| 20 | When external emergency stop is entered |
| 21 | When internal emergency stop is entered |
| 22 | When external H/W lower limit switch is input |
| 23 | When external H/W upper limit switch is input |
| 24 | Current position exceeding lower boundary of S/W address range. |
| 25 | Current position exceeding upper boundary of S/W address range. |
| 26 | A number other than original operation mode number is entered. |
| 27 | Positioning data address exceeding the allowed range. |
| 28 | Dwell time exceeding the allowed range. (0~999) |
| 36 | The operation following automatic or continuous operation is incorrect. |
| 37 | Interpolation operation is selected during continuous, constant speed or positioning constant speed operation. |

| Error code | Description |
| --- | --- |
| 48 | Deceleration-related control issued during JOG or RTP control execution |
| 49 | Deceleration-related control issued during Dwell zeroing. |
| 56 | NM, OR or speed change control issued when not in constant speed phase by operation control. |
| 57 | NM or OR control issued in constant speed or positioning constant speed operation. Speed change control issued in continuous, constant speed or positioning constant speed operation |
| 58 | NM control issued in modes other than continuous operation mode. |
| 59 | N-M control issued when not in operation. |
| 60 | OR control issued but OR is set invalid. |
| 61 | Rotation direction can be changed with N_M control. |
| 66 | Out of positioning data to proceed with Data number exceeding the range when position teaching or speed teaching control issued |
| 67 | OR value in percentage exceeding allowed range 1~55(x 10%). |
| 68 | Inposition value exceeding allowed range (-999 ~ +999). |
|  | Inching value exceeding allowed range (1 ~ 99). |
| 69 | Position address set with preset control exceeding upper or lower limits. |
| 76 | Operation control issued when zero point is not decided and data type is absolute. |
| 77 | Position teaching control is entered when zero point is not decided. |
| 86 | Speed exceeding the range. (faster than the maximum speed, slower than the bias speed, or set as “0) |
| 87 | Lower speed of zeroing set faster than the higher speed or slower than the bias speed |
| 88 | Short cut speed calculated with line interpolation exceeding allowed range |
| 89 | Constant speed or deceleration time exceeding allowed range (Max. 65,535 ms) |
| 96 | A control issued when output is prohibited |
| 97 | A control issued during busy |
| 98 | Zeroing and start interpolation controls are issued when CPU module is stopped. |
| 106 | Parameter data are incorrect. |
| 107 | Data manipulation result exceeding the range |
| 116 | Exceeding variation counter range |
| 126 | Synchronous operation mode error |
| 127 | Station number setting error |
| 136 | Slave-axis failure |
| 137 | 485 communication error |
| 138 | Incorrect configuration of synchronous axis |
| 146 | Radius input exceeding the range in circular arc interpolation operation |

## 9.2 Trouble diagnosis

### 9.2.1 Positioning operation error

### 9.2.2 Positioning speed is different from the setting speed

### 9.2.3 Abnormal stop during positioning

### 9.2.4 Zeroing error

# Text boxes

Yes

Yes

Yes

No

No

No

No

Yes

Check the wiring of zero point limit switch

H/W failure

Contact the service center

E N D

Servo drive failure

Z-phase signal output from servo driver?

Z-phase signal on?

Zeroing speed changed to low?

Is zero point limit switch on?

Monitor zeroing status with a software package

Zeroing error

No

No

Yes

Yes

Yes

No

No

Contact the service center

Drive failure

Stop?

E N D

Establish measures for noise

Stop?

Operate after pausing the noise source.

Is there a noise source?

Check if noise sources like

Remove the program and start again.

Yes

Pause program exists.

Check if pause-related command exists in PLC program.

Abnormal stoppage during positioning

Yes

No

No

No

Yes

No

Yes

Yes

Yes

H/W failure

Contact Service center.

Speed change by override, next move or speed change common

Speed changes depending on moving distance(not error)

Set setting speed slower than speed limit.

Enter correct data value.

E N D

Same with the setting value?

Check external output.

Has PLC scents speed change command?

Interpolation

Operation?

Setting speed > Speed limit

Check parameter, positioning data and speed data setting.

No

Positioning setting speed is different from the actual speed.

Set

Correctly?

Yes

Yes

Yes

No

Yes

No

No

No

Drive unit failure

Re-wire positioning module and drive unit.

Adjust pulse output mode(type A,B) of parameter as for drive unit

Set to run mode

E N D

H/W failure

Contact service center.

Is external output normal?

Are positioning module and drive correctly wired?

Corresponds to drive unit?

Check pulse output mode.

RUN

Check PLC CPU mode.

Yes

Positioning not executed.

Manual

Operation?