1. Features

1.1 Characteristics of Smart I/O

1) The characteristics of Smart I/O series is as follows.

(1) Product design based on International Electrotechnical Commission (IEC 61131)

(GLOFA series in common)

 Easy support to programming device

 Standard language (IEC 61131-3) provided (IL / LD / SFC)

(2) Open network by selecting international standard communication protocol.

(3) Available to communicate with remote master module independently without power module/CPU module.

(4) Available to set maximum 32 ~ 64 stations.

- Maximum 64 stations (Rnet, Dnet)

- Maximum 32 stations (Pnet, Snet)

(5) Enables to save the cost for installation and maintenance.

(6) Various system configuration and simple maintenance and repair.

(7) Easy to change the system.

(8) Compatible with other maker’s product.

- Available to connect Smart I/O to other maker’s master.

(9) Easy to set the system as the station address setting by hardware is available.

(10) Simple communication programming.

- Using the GMWIN/KGLWIN high speed link parameter

- But for Modbus, using function block

(11) Supports various I/O.

- DC input 16/32 points, TR output 16/32 points, Relay output 16 points

(12) Supports various OPEN type communication method.

- Profibus-DP, DeviceNet, Rnet, Modbus

(13) Easy to configure and use as integrating PLC.

- Packaged by one unit including CPU, I/O and communication function.

(14) Provides the online network status detection function.

- Available to know the remote module status through high speed link monitor.

(15) Supports high speed communication.

(16) Flexible communication relation is available as the speed shall be set automatically according to the speed of master.

- Profibus-DP, DeviceNet etc.

2. Specifications

2.1 General Specifications

| No | Items | Specification |  |  |  |  |  |  | References |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Use Temp. | 0 ~ 55 C |  |  |  |  |  |  |  |
| 2 | Storage Temp. | 25 ~ 70 C |  |  |  |  |  |  |  |
| 3 | Use humidity | 5 ~ 95%RH, no dew |  |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, no dew |  |  |  |  |  |  |  |
| 5 | Vibration-resistant | In case of Intermittent vibration |  |  |  |  |  | - |  |
|  |  | Frequency |  | Acceleration |  | Amplitude |  | Times | IEC6 1131-2 |
|  |  | 10  f  57Hz |  |  |  | 0.075mm |  | X, Y, Z 10 times each direction |  |
|  |  | 57  f  150Hz |  | 9.8m/s2{1G} |  |  |  |  |  |
|  |  | In case of Continuous vibration |  |  |  |  |  |  |  |
|  |  | Frequency |  | Acceleration |  | Amplitude |  |  |  |
|  |  | 10  f  57Hz |  |  |  | 0.035mm |  |  |  |
|  |  | 57  f  150Hz |  | 4.9m/s2{0.5G} |  |  |  |  |  |
| 6 | Impact-proof |  max. impact acceleration: 147 m/s2{15G}  Application time: 11ms  pulse wave type: semi-sine wave pulse (3 times each direction X, Y, Z) |  |  |  |  |  |  | IEC 61131-2 |
| 7 | Noise-resistant | Square wave impulse noise | AC:  1,500 V, DC: 900 V |  |  |  |  |  | LGIS internal test reference |
|  |  | Electrostatic discharge | Voltage: 4kV (Touch discharge) |  |  |  |  |  | IEC 61131-2, IEC 801-2 |
|  |  | Radiant electromagnetic field noise | 27 ~ 500 MHz, 10 V/m |  |  |  |  |  | IEC 61131-2, IEC 801-3 |
|  |  | Fast Transient / Bust Noise | Classification | Power module | Digital I/O (more than 24V ) |  | Digital I/O (below 24V) Analog I/O Communication Interface |  | IEC 61131-2 IEC 801-4 |
|  |  |  | Voltage | 2kV | 1kV |  | 0.25kV |  |  |
| 8 | Surrounding environment | No corrosive gas, no dust |  |  |  |  |  |  |  |
| 9 | Use altitude | Less than 2,000m |  |  |  |  |  |  |  |
| 10 | Pollution | Less than 2 |  |  |  |  |  |  |  |
| 11 | Cooling method | Natural air-conditioning |  |  |  |  |  |  |  |

1) IEC (International Electrotechnical Commission)

: International civil community that promotes international cooperation for standardization of electric/electro

technology, publishes international standard and operates suitability assessment system related to the above.

2) Pollution Degree

: An index that indicates the pollution degree of used environment that determines the insulation performance of the device. For example, pollution degree 2 means the state to occur the pollution of non-electric conductivity generally, but the state to occur temporary electric conduction according to the formation of dew.

Remarks

2.2 Power Specifications

| Items | Specification |
| --- | --- |
| Input power | DC +24V (Max +28V, Min +19V) |
| Input current | 0.4A(+24VDC) |
| Dash current | Less than 40A: (24VDC input) |
| Rated output current (+5V) | 0.2~0.6A |
| Efficiency | More than 60% (in case of Full Load) |
| Power indication | When power input, LED ON |
| Output voltage dwell time | Within 150ms (DC19~24V input, Full Load) |
| Suitable wire spec | 1.5 ~ 2.5mm2 (AWG16 ~ 22) |
| Suitable tightening torque | 12kg  cm |

2.2 Input Specifications

| Items |  | DC Input |  | Hybride |
| --- | --- | --- | --- | --- |
| Input Points |  | 16 | 32 | 16 |
| Insulation method |  | Photo coupler insulation |  |  |
| Rated Input Voltage |  | DC 24V |  |  |
| Rated Input Current |  | 7mA |  |  |
| Available Voltage Range |  | DC 20.4~28.8V (Ripple rate: within 5% ) |  |  |
| On Voltage/Current |  | 19V/3.5mA |  |  |
| Off Voltage/Current |  | 16V/1.5mA |  |  |
| Input Resistance |  | Approx. 3.3 ㏀ |  |  |
| Response Time | Off  On | Less than 3ms |  |  |
|  | On  Off | Less than 3ms |  |  |
| External Cabling type |  | Sink/Source |  |  |
| Points/Common |  | 16Points/1Common |  |  |
| Consumption Current |  | 200mA | 300mA | 350mA |
| Network & Module Name | Rnet | GRL-D22A | GRL-D24A | GRL-DT4A |
|  | Profobus-DP | GPL-D22A | GPL-D24A | GPL-DT4A |
|  | DeviceNet | GDL-D22A | GDL-D24A | GDL-DT4A |
|  | Modbus | GSL-D22A | GSL-D24A | GSL-DT4A |

2.3 Output Specifications

| Module Type |  |  | Tr Output |  | Ry Output |  | Hybride |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Output Device |  |  | Transistor |  | Relay |  | Transistor |
| Output Points |  |  | 16 | 32 | 16 | 32 | 16 |
| Insulation method |  |  | Photo coupler insulation |  | Relay insulation |  | Photo coupler |
| Rated load Voltage |  |  | DC 24V |  | DC 24V AC220V |  | DC 24V |
| Rated load Current |  |  | 0.1A/P, 2A/Com |  | 2A/P, 5A/Com |  | 0.1A/P, 2A/Com |
| Available load Voltage |  |  | DC 20.4~26.4V (Ripple rate: within 5%) |  | DC 5~110V AC 250V Max. |  | DC 20.4~26.4V |
| Max. Inrush Current |  |  | Less than 4 A / 10 ms |  |  |  | Less than 4 A / 10 ms |
| Max. Voltage drop when ON |  |  | DC 1V |  |  |  |  |
| Max. Leakage Current |  |  | 0.1mA |  |  |  |  |
| Serge Killer |  |  | Clamp diode |  | - |  | - |
| Response Time |  | Off  On | Less than 2ms |  | Less than 10ms |  | Less than 2ms |
|  |  | On  Off | Less than 2ms |  | Less than 12ms |  | Less than 2ms |
| Points/Common |  |  | 16 |  | 8 |  | 16 |
| Consumption Current |  |  |  |  |  |  |  |
| Network & Module Name | Rnet |  | GRL-TR2A | GRL-TR4A | GRL-RY2A |  | GRL-DT4A |
|  | Profobus-DP |  | GPL-TR2A | GPL-TR4A | GPL-RY2A |  | GPL-DT4A |
|  | DeviceNet |  | GDL-TR2A | GDL-TR4A | GDL-RY2A |  | GDL-DT4A |
|  | Modbus |  | GSL-TR2A | GSL-TR4A | GSL-RY2A |  | GSL-DT4A |

2.4 Type Name Indication

G

L

A

Communication type

P: Profibus-DP

D: DeviceNet

R: Rnet

S: Modbus

L: Communication

I/O Type

D2: DC24V input

RY: Relay output

TR: TR output

DT: DC input/ TR output

I/O points

2: 16 points

4: 32 points

Char.

class

G

2.5 Version Compatibility Table for

The followings describe the list that enables the compatibility of O/S version between various CPU and master module to use Smart I/O series.

Before using the product, please refer to the list below and apply it to system configuration.

| Classification | Model type | Available O/S |
| --- | --- | --- |
| CPU | GM3 | More than Version 2.5 |
|  | GM4 | More than Version 2.6 |
|  | GM6 | More than Version 1.9 |
|  | GM7 | More than Version 1.6 |
|  | K1000S | More than Version 3.1 |
|  | K300S | More than Version 3.1 |
|  | K200S | More than Version 2.2 |
|  | K80S | More than Version 1.6 |
| PADT | GMWIN | More than Version 3.6 |
|  | KGLWIN | More than Version 3.3 |
| Smart I/O Master | Profibus-DP | More than Version 1.0 |
|  | DeviceNet | More than Version 1.2 |
|  | Rnet | More than Version 1.0 |
|  | Modbus | More than Version 2.0 |