1. Features

- Supports RS-232C and RS-422/485 channels and they can operate as independent

(stand-alone)mode or concurrent(interlocking) mode.

- Supports various communication speed (baud rate) from 300bps to 57,600bps (RS-422)

- Supports a multi-drop function that maximum 32 station can be joined into a network

- A frame editor software that are based on MS-Windows 95/98 is provided. User can write

an user-defined protocol for communication with other manufacturer’s PLCs.

- With a modem communication function, it can control a remote PLC by dedicated protocol, or

user-defined protocol.

- In a main base board, multiple Cnet modules can be mounted.

(GM6 / K200S : 2 modules, GM4 / K300S : 4 modules, GM3 / K1000S : 8 modules)

2. Specification

2-1 Performance Specification

| CPU | GM1/2/3 (K1000S) | GM4 (K300S) | GM6 (K200S) | GM7 (K80S) |
| --- | --- | --- | --- | --- |
| Communication Module | G3L-CUEA | G4L-CUEA | G6L-CUEB G6L-CUEC | CPU Built in | G7L-CUEB G7L-CUEC | CPU Built in |
| Interface | RS-232C RS-422/485 | RS-232C RS-422/485 | RS-232C | RS-232C RS-422/485 | RS-232C |
| Channel Operation (Valid only for 2ports) | Independent / Concurrent Selectable | - |
| Comm. Service | Dedicated Protocol | ● |
|  | User Defined Protocol | ● | Ｘ | ● |
|  | AB DF1 | ○ (Works only as slave) | Ｘ | Ｘ |
|  | Modbus | ○ (Works only as slave) | Ｘ | ● (Master/Slave Selectable) |
| Modem Communication | Available through RS-232C Port |
| Data Structure | Data Bit | 7 or 8 |
|  | Stop Bit | 1 or 2 |
|  | Parity | Even, Odd, None |
| Transmit Speed | RS-232C | 300 / 600 / 1200 / 2400 / 4800 / 9600 / 19200 / 38400bps |
|  | RS-422/ 485 | 300 / 600 / 1200 / 2400 / 4800 / 9600 / 19200 / 38400 / 57600bps |
| Transmit Distance | RS-232C | 15m (Max) |
|  | RS-422/ 485 | 500m (Max) |
| Connection | RS-232C | 1:1 |
|  | RS-422/ 485 | 1:N (N = Slave Station, Max 32) |

2-2 Parts Name and Description

2-2-1 G3L-CUEA

2-2-2 G4L-CUEA

2-2-3 G6L-CUEB

2-2-4 G6L-CUEC

2-2-5 G7L-CUEC

| No | Name | Contents |
| --- | --- | --- |
| ① | RS-422/485 Interface | RS-422/485 Connector for connection with external devices |
| ② | LED Display | TX, RX, Power Display LED |
| ③ | Expansion Connector | Expansion Connector for connection with Other Special Module (A/D, HSC …) |

2-3 Communication Mode Setting

2-3-1 Off Line mode switching (Switching by H/W switch)

The operation mode of Cnet module is set by a rotary switch at the front panel of the module. The Cnet

module will read the switch status and set the operation mode when the power is supplied. To change

the operation mode of Cnet module, therefore, make sure to cycle the power of Cnet module after

mode switch setting.

1) In case of G3L-CUEA / G4L-CUEA

| Mode switch | Switch position | Operation mode | Remarks |
| --- | --- | --- | --- |
|  |  | RS-232C | RS-422 |  |
|  | 0 | User-defined | User-defined | Concurrent mode (Interlocking mode) 1) |
|  | 1 | Dedicated | Dedicated |  |
|  | 2 | User-defined | User-defined | Independent mode (Stand-alone mode) |
|  | 3 | Dedicated | Dedicated |  |
|  | 4 | User-defined | Dedicated | Independent mode (Stand-alone mode) 2) |
|  | 5 | Dedicated | User-defined |  |
|  | 6 | Loader I/F | User-defined |  |
|  | 7 | Loader I/F | Dedicated |  |
|  | 8 | Loop-back | Loop-back | Self-diagnosis |
|  |  | Flash memory write | Press the ‘display’ button at the power-on |
|  | 9 | On-line | On-line mode change |

2) In case of G6L-CUEB / G6L-CUEC

| Mode switch | Switch position | Operation mode | Remarks |
| --- | --- | --- | --- |
|  | 0 | User-defined |  |
|  | 1 | Dedicated |  |
|  | 2 | Loader I/F |  |
|  | 3 | Loop-back |  |
|  | 4 | Reserved | Not used |
|  | 5 |  |  |
|  | 6 |  |  |
|  | 7 |  |  |
|  | 8 | Flash memory write | Cnet v2.0 or later |
|  | 9 | On-line | On-line mode change |

2-3-2 On Line mode switching (Switching by S/W)

Operation mode can be switched by software(Cnet Frame Editor Ver. 2.0)

For use this function, rotatry switch of Cnet module should be placed on ‘9’

Library mode(Modbus/AB DF1 Service) can be selected in Online mode only.

3. System Configuration and Cabling

3-1 RS-232C

3-1-1 Connection between Cnet Module (G3L-CUEA, G4L-CUEA, G6L-CUEA)

and External Device

1) In case that external device uses CD signal (Use handshake function)

| Cnet (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

2) In case that external device doesn’t uses CD signal (No handshake function)

| Cnet (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

3-1-2 Connection between Cnet Module (G3L-CUEA, G4L-CUEA, G6L-CUEA)

and Modem

| Cnet (9-pin) | Pin connection and signal direction | Modem (25-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 8 | CD |
| 2 | RxD |  | 3 | RxD |
| 3 | TxD |  | 2 | TxD |
| 4 | DTR |  | 20 | DTR |
| 5 | SG |  | 7 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 4 | RTS |
| 8 | CTS |  | 5 | CTS |
| 9 | RI |  | 22 | RI |

3-1-3 Connection between Cnet Modules (G3L-CUEA, G4L-CUEA, G6L-CUEA)

| Cnet (9-pin) | Pin connection and signal direction | Cnet (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

3-1-4 Connection between GM6(K200S)/GM7(K80S) CPU Port (Cnet Built in)

and External Device

| CPU (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

3-1-5 Connection between GM6(K200S)/GM7(K80S) CPU Port (Cnet Built in)

and PMU

| CPU (9-pin) | Pin connection and signal direction | PMU (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

3-1-6 Connection Between GM7(K80S)CPUs (Cnet Built in)

| CPU (9-pin) | Pin connection and signal direction | CPU (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

♠Point !!!

Using Loader function and Cnet synchronously (GM7/K80S)

- In case of using built in Cnet

Connection#1 (RS232C/Cnet)

| CPU (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

Connection#2 (RS232C/Loader)

| CPU (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

- In case of using option module(G7L-CUEB)

Connection#1 (RS232C/Cnet) : In case of no handshake fuction

| Cnet (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

Connection#2 (RS232C/Loader)

| CPU (9-pin) | Pin connection and signal direction | External device (9-pin) |
| --- | --- | --- |
| Pin No. | Name |  | Pin No. | Name |
| 1 | CD |  | 1 | CD |
| 2 | RxD |  | 2 | RxD |
| 3 | TxD |  | 3 | TxD |
| 4 | DTR |  | 4 | DTR |
| 5 | SG |  | 5 | SG |
| 6 | DSR |  | 6 | DSR |
| 7 | RTS |  | 7 | RTS |
| 8 | CTS |  | 8 | CTS |
| 9 | RI |  | 9 | RI |

3-2 RS-422/485

3-2-1 1 : 1Connection

1) In Case of G3L-CUEA / G4L-CUEA / G6L-CUEA

⊙RS-422 Connection                          ⊙RS-485 Connection

2) In Case of G7L-CUEC

⊙RS-422 Connection                          ⊙RS-485 Connection

3-2-2 Multidrop(1:N) Connection

1) In Case of G3L-CUEA / G4L-CUEA / G6L-CUEA

⊙RS-422 Connection

⊙RS-485 Connection

2) In Case of G7L-CUEC

⊙RS-422 Connection

⊙RS-485 Connection

4. Communication Service

| CPU | GM1/2/3 (K1000S) | GM4 (K300S) | GM6 (K200S) | GM7 (K80S) |
| --- | --- | --- | --- | --- |
| Communication Module | G3L-CUEA | G4L-CUEA | G6L-CUEB G6L-CUEC | CPU Built in | G7L-CUEB G7L-CUEC | CPU Built in |
| Dedicated Service (PLC( Ex.Device) | Master & Slave | Slave |
|  | S/W Tool | Cnet Editor | GMWin or KGLWin |
|  | Parameter | Basic Parameter | Comm. Parameter |
|  | PLC Prog. | Not required |
| Dedicated Service (PLC( PLC) | Master & Slave | Master/Slave (One station works as a master, the other one works as a slave) |
|  | S/W Tool | Cnet Editor | GMWin or KGLWin |
|  | Parameter | Basic Parameter | HS Link (RS485/422 Only) | Comm. Parameter |
|  | PLC Prog. | Master : GM_RD/GM_WR(GLOFA) READ/WRITE(Master K) Slave : Not required. | Not required | Not required |
| User Define Service (PLC( Ex.Device) | Master & Slave | Master | Not support | Master |
|  | S/W Tool | Cnet Editor | Not support | GMWin or KGLWin |
|  | Parameter | Basic Parameter & Frame Editing | Not support | Comm. Parameter |
|  | PLC Prog. | SND_MSG/RCV_MSG(GLOFA) SND/RCV(Master K) | Not support | SND_MSG |
| Library Service (Modbus) | Master & Slave | Slave | Not support | Master/Slave |
|  | S/W Tool | Cnet Editor | Not support | GMWin or KGLWin |
|  | Parameter | Library Downloading | Not support | Comm. Parameter |
|  | PLC Prog. | Not required | Not support |  |
| Library Service (AB DF1) | Master & Slave | Slave | Not support |
|  | S/W Tool | Cnet Editor | Not support |
|  | Parameter | Library Downloading | Not support |
|  | PLC Prog. | Not required | Not support |

4-1. Dedicated Protocol Service

4-1-1 Introduction

Cnet module includes a dedicated protocol for communication with external devices.

It enables that an external device reads/writes data from/to PLC CPU through Cnet module if the external

device send a data frame complying with the dedicated protocol.

- During this service Cnet module works as only a slave for external device, so any PLC program

to related with communication is not required.

2) RS-232C and RS-422 channels can communicate independently or concurrently according to mode

setting.

3) Multi-drop network is available by assigning a station number to Cnet modules.

(Max. 32 station can be connected.)

4) By using dedicated Function Block(GM_RD, GM_WR) or Instruction(READ, WRITE), communication

can be executed easily between GLOFA(Master K) PLCs. (Cnet Ver.2.0 or higher)

4-1-2 Operation Flow

- External device(PC, MMI etc…) sends the command frame created by user application software

to PLC Cnet module via RS-232C or 422/485 port.

- Communication Processor of Cnet module analyze and checks command frame.

- Datas requested by external device are exchanged between Cnet module and PLC CPU.

- Cnet module sends the response frame to external device.

4-1-3 Dedicated Protocol Frame Structure

4-1-3-1 Basic structure

- Request frame (External device ( Cnet module)

| Header (ENQ) | Station number | Command | Command type | Structured data area | Tail (EOT) | Error check (BCC) |
| --- | --- | --- | --- | --- | --- | --- |

- ACK Response Frame (Cnet Module ( External device)

| Header (ACK) | Station number | Command | Command type | Structured data area or Null | Tail (ETX) | Error check (BCC) |
| --- | --- | --- | --- | --- | --- | --- |

- NAK Response Frame (Cnet Module ( External device)

| Header (NAK) | Station number | Command | Command type | Error code (ASCII 4 bytes) | Tail (ETX) | Error check (BCC) |
| --- | --- | --- | --- | --- | --- | --- |

4-1-3-2 Command & Command type

|  | Command | Type | Description |
| --- | --- | --- | --- |
|  |  |  | GLOFA | Master K |
| Read | Single | r (R) | SS | Read a single Bit / Byte Word / Double word from PLC | Read a single Bit / Word from PLC |
|  | Continuous | r (R) | SB | Read multiple Byte Word / Double word From PLC (Bit signal is not available) | Read multiple Words from PLC (Bit signal is not available) |
| Write | Single | w (W) | SS | Write a single Bit / Byte Word / Double word to PLC | Write a single Bit / Word To PLC |
|  | Continuous | w (W) | SB | Write multiple Byte Word / Double word to PLC (Bit signal is not available) | Write multiple Words to PLC (Bit signal is not available) |

4-1-3-3 Device Memory Expression

|  | Item | Memory Expression | Remarks |
| --- | --- | --- | --- |
|  |  | Bit | Byte | Word | Double |  |
| GLOFA | Input | %IX0.0.0~ | %IB0.0.0~ | %IW0.0.0~ | %ID0.0.0~ | Read / Write |
|  | Output | %QX0.0.0~ | %QB0.0.0~ | %QW0.0.0~ | %QD0.0.0~ | Read / Write |
|  | Internal Memory | %MX000~ | %MB000~ | %MW000~ | %MD000~ | Read / Write |
| Master K | Input & Output | %PX000~ | - | %PW000~ | - | Read / Write |
|  | Internal Relay | %MX000~ | - | %MW000~ | - | Read / Write |
|  | Keep Relay | %KX000~ | - | %KW000~ | - | Read / Write |
|  | Special Relay | %FX000~ | - | %FW000~ | - | Read Only |
|  | Timer | %TX000~ | - | %TW000~ | - | Read / Write |
|  | Counter | %CX000~ | - | %CW000~ | - | Read / Write |
|  | Data Register | - | - | %DW000~ | - | Read / Write |

4-1-3-4 Read continuous device memory (RSB Command)

1) Request Format (External Device ( Cnet Module)

2) ACK Response Format (Cnet Module ( External Device)

3) NAK Response Format (Cnet Module ( External Device)

- Station number, command, and type are same as the request format.

- BCC : When the command is small character (r), the lower byte of summation from ENQ to EOT is

converted into ASCII format and added to frame as BCC check.

- Length of device definition : It indicates that the device definition include ‘%’ occupies how many bytes

after converted to ASCII code (1byte = 2 ASCII codes). The available range is h01 ~ h10

( ASCII format : h3031 ~ h3130 )

For Example : %MW000 = h06,  %PW0000 = h07

- Device definition : It indicates an actual address to be read. It should be consist of ‘%’, device type

(capital or small letter), and numbers only.

- Number of data (in the Request) : It indicates that how many bits/bytes/words/double words will be read

from the start address. The unit of this value is dependant on Device memory(Variable) type

The range is h01 ~ h3C (1 ~ 60).

- Number of data (in the Response) : It indicates the size of datas received in the unit of Byte.

- Block Number of ACK Response is only available for GLOFA CPU and always set to “01”.

4-1-4 Dedicated Function Block(GLOFA) & Instruction(Master K)

- This function block and instruction is only available for communication between GLOFA’s Cnet

Modules or Master K’s Cnet modules

- When you want to communicate with multi-stations for RS-422 Channel, you should make a program to

be communicated in order. (this is to prevent data collision error)

- Reading/Writing is available up to 110 bytes

4-1-4-1 Function Block (for GM1/2/3/4/6)

4-1-4-1 Instruction (for K1000S/300S/200S)

|  | Description |
| --- | --- |
| sl | Slot number on which the Cnet module is mounted |
| st | Station number of other station and communication channel (4words) Ex) In case that ‘D000’ is designated - D000~D001 (2words) : Station number of other station to accessed - D002~D003 (2words) : Channel selection (0:RS-232C, 1:RS-422/485) |
| D | Head Device address of self-station at which read data is stored (in case of ‘READ’) Head Device address of self-station at which write data is stored (in case of ‘WRITE’) |
| S | Head Device address of other station to be read (in case of ‘READ’) Head Device address of other station to be written (in case of ‘WRITE’) |
| n | Numbers of word to be read |
| SS | Device at which the communication status is stored |

| Instructions | Available Device | Steps |
| --- | --- | --- |
|  | M | P | K | L | F | T | C | S | D | #D | Integer |  |
| READ | sl |  |  |  |  |  |  |  |  |  |  | O | 13 |
|  | St | O | O | O | O | O | O | O |  | O | O |  |  |
|  | D | O | O | O | O* |  | O | O |  | O | O |  |  |
|  | S | O | O | O | O | O | O | O |  | O | O |  |  |
|  | n |  |  |  |  |  |  |  |  | O |  | O |  |
|  | SS | O | O | O | O* |  | O | O |  | O | O |  |  |

4-2. User Defined Protocol Service (FB Service)

4-2-1 Introduction

User defined protocol service is used when the external device has a different protocol form from

Cnet module and user intend to communicate with external devices by using their own protocol.

- During this service Cnet module works as a master for external device, so PLC program which

sends/receives communication frame is required.

- Communication frame can be easily created by frame editor tool and that frame file can be used

with Function Block in user’s PLC program.

- This service is mainly used for communicating between PLC and other device which has RS-232C

or RS-422/485 port and opened protocol format.

4-2-2 Operation Flow

- By using function block(GLOFA CPU : SND_MSG) or instruction(Mater K : SND) PLC CPU sends

the command frame created by frame editor tool to Cnet module.

② Cnet module sends the command frame to external device via RS-232C or RS-422/485 port.

③ External device sends the response frame requested to Cnet module.

④ By using function block(GLOFA CPU : RCV_MSG) or instruction(Master K : RCV) PLC CPU receives

the response frame from Cnet module

4-2-3 Function Block & Instruction

4-2-3-1 Function Block (GLOFA CPU)

1) SND_MSG (Send Message)

| Input | Output |
| --- | --- |
| REQ (Bool) | When input condition changes 0 to 1, (rising edge), executes 1 time | NDR (Bool) | Turns on when FB is executed normally. |
| SLOT_NO (Sint) | Slot No. at which Cnet Module is In mounted | ERR (Bool) | Turns on when FB is executed abnormally |
| CH (Usint) | 0 : RS-232C 1 : RS-422/485 | STATUS (Usint) | Detail error code (0 is Normal status) |
| FNAM (String) | Send frame name configured by frame editor |  |  |
| SD n n=1,2,3,4 (Usint Array) | Array Variable to be sent (Even if all field (SD1~SD4) is not Used, must be filled by dummy Array variables) |  |  |
| LEN n n=1,2,3,4 (Usint) | Number of Array Variable to be Sent |  |  |

2) RCV_MSG (Receive Message)

| Input | Output |
| --- | --- |
| REQ (Bool) | When input condition changes 0 to 1, (rising edge), executes 1 time | NDR (Bool) | Turns on when FB is executed normally. |
| SLOT_NO (Sint) | Slot No. at which Cnet Module is In mounted | ERR (Bool) | Turns on when FB is executed abnormally |
| CH (Usint) | 0 : RS-232C 1 : RS-422/485 | STATUS (Usint) | Detail error code (0 is Normal status) |
| FNAM (String) | Receive frame name configured by frame editor | LEN n n=1,2,3,4 (Usint) | Displays the byte number of datas To be received |
| RD n n=1,2,3,4 (Usint Array) | Array Variable to be stored (Even if all field (RD1~RD4) is not Used, must be filled by dummy Array variables) |  |  |

4-2-3-2 Instruction (Master K CPU)

1) SND

|  | Description |
| --- | --- |
| sl | Slot number of Cnet module mounted & Type of channel (RS232C or RS422) - Lower 8 bits (CD) : Slot No. of Cnet module mounted - Higher 8 bits (AB) : Type of channel (h00 : RS232C, h01 : RS422) |
| Fnam | Send frame name configured by frame editor (8words, ASCII Code) |
| snd | Start address of device that stores source data to be sent |
| n | Numbers of byte to be sent |
| SS | Device at which the communication status is stored |

2) RCV

|  | Description |
| --- | --- |
| sl | Slot number of Cnet module is mounted & Type of channel (RS232C or RS422) - Lower 8 bits (CD) : Slot No. of Cnet module mounted - Higher 8 bits (AB) : Type of channel (h00 : RS232C, h01 : RS422) |
| Fnam | Receive frame name configured by frame editor (8words, ASCII Code) |
| rcv | Start address of device that stores source data to be received |
| n | Numbers of byte to be received |
| SS | Device at which the communication status is stored |

4-3. Library Service (Modbus / AB DF1 Service)

4-3-1 Introduction

To communicate with other manufacturer’s PLC without writing an user-defined frame, the ‘Library service’

Is added to the Cnet module v2.0.

In the library mode, the Cnet module will communicate with other manufacturer’s device according to the

library downloaded to the Cnet module, and no frame setting is required. (Set basic parameters only)

The frame editor includes two libraries for AB DF1(AB Asynchronous Full Duplex) and Modbus.

With these libraries, the Cnet module can operate as a ‘Slave(Server)’ or ‘Master(Client)’ station.

| CPU | GM1/2/3 (K1000S) | GM4 (K300S) | GM6 (K200S) | GM7 (K80S) |
| --- | --- | --- | --- | --- |
| Communication Module | G3L-CUEA | G4L-CUEA | G6L-CUEB G6L-CUEC | CPU Built in | G7L-CUEB G7L-CUEC | CPU Built in |
| Modbus | Master | Ｘ | Ｘ | ● |
|  | Slave | ● | Ｘ | ● |
| AB DF1 | Master | Ｘ | Ｘ | Ｘ |
|  | Slave | ● | Ｘ | Ｘ |
| Library | Ab34.lib Modbus6.lib | Ab6.lib modbus6.lib | - | Library Download is not required |

4-3-2 Library Download

① Set the Cnet module to ‘Flash memory write mode’ with the mode selection switch.

② the LED of Cnet module will blink with 1 second period.

③ Run the frame editor and connect to the Cnet module. Then, select File – Open Lib in menu.

④ Select a library file to be downloaded as following figure

⑤ select Online – Flash Memory – Write in the menu. Type the slot number at which the Cnet module

is mounted, and press ‘Write’ button.

5. Operation Procedure

6. Example

6-1 Dedicated protocol service (GM6 / K200S ( IBM PC)

6-1-1. Example Overview

By using Cnet dedicated protocol, IBM PC reads data memory In the PLC CPU and displays

results on the monitor screen.

6-1-2. System Configuration

6-1-3. Test Environment

|  | Computer | GM6 / K200S |
| --- | --- | --- |
| CPU | Pentium 133 | GM6 CPU / K200S CPU |
| Communication Module | COM1 Port | G6L-CUEA |
| Cable | RS-232C | RS-232C |
| O/S | Windows95 | - |
| Development Language | MS Visual Basic | - |
| Station number | - | 0 |
| Mode Switch | - | 1 (RS-232C Dedicated) |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Cnet Dedicated Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-1-4. Setting Cnet Basic Parameter

- Cnet frame editor tool is consist of two part, Basic parameter and Frame list.

- In part of basic parameter, the parameter related Cnet is decided

- In case of dedicated protocol service, frame list is not required to be set.

6-1-5. Computer Application Sample Software (Developed by visual basic)

- Set COM Port, Baudrate, Parity, Data Bit, Stop Bit (These parameter values must be same as the

Value of the Cnet basic parameter set by frame editor)

2) Set Request frame (00RSB06%DW10005)

3) Click ‘OPEN’ button.

4) Click ‘SEND’ button.

5) Response will be displayed on ‘Rx’ menu.

6-3 Dedicated protocol service (K200S ( K200S)

6-3-1. Example Overview

By using Cnet dedicated protocol, K200S(Master) reads data memory(D100 ~ D104) of K200S(Slave)

CPU and stores that value in D200 ~ D204.

6-3-2 System Configuration

6-3-3. Test Environment

|  | K200S | K200S |
| --- | --- | --- |
| CPU | K200S CPU | K200S CPU |
| Communication Module | G6L-CUEA | G6L-CUEA |
| Cable | RS-232C | RS-232C |
| Programming (Instruction) | READ / WRITE | Not required |
| Station number | 0 | 1 |
| Mode Switch | 1 (RS-232C Dedicated) | 1 (RS-232C Dedicated) |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Cnet Dedicated Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-3-4. Setting Cnet Basic Parameter

1) Station 0

2) Station 1

6-3-5. PLC Programming (Station 0)

6-4 Dedicated protocol service (GM6 ( GM6)

6-4-1. Example Overview

By using Cnet dedicated protocol, GM6(Master) reads data memory(%MB100 ~ %MB103) of GM6(Slave)

CPU and stores that value in %MB0 ~ %MB3.

6-4-2 System Configuration

6-4-3. Test Environment

|  | GM6 | GM6 |
| --- | --- | --- |
| CPU | GM6 CPU | GM6 CPU |
| Communication Module | G6L-CUEA (Slot 5) | G6L-CUEA (Slot 5) |
| Cable | RS-232C | RS-232C |
| Programming (Instruction) | GM_RD | Not required |
| Station number | 0 | 1 |
| Mode Switch | 1 (RS-232C Dedicated) | 1 (RS-232C Dedicated) |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Cnet Dedicated Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-4-4. Setting Cnet Basic Parameter

1) Station 0

2) Station 1

6-4-5. PLC Programming (Station 0)

1) Library Inserting

- Select “Project ( Library insert” on GMWin menu.

- Click Add  then select “communi.6fb”

2) Programming

6-5 Dedicated protocol service (GM7 ( GM7)

6-5-1. Example Overview

By using Cnet dedicated protocol, GM7(Master) reads data memory(%IW0.0.0) & write data memory

(%QW0.0.0) of GM7(Slave)

By setting parameter only, communication is executed easily (Ladder program is not required)

6-5-2 System Configuration

6-5-3. Test Environment

|  | GM7 | GM7 |
| --- | --- | --- |
| CPU | GM7 CPU | GM7 CPU |
| Communication Module | CPU Built in | CPU Built in |
| Cable | RS-232C | RS-232C |
| Programming (Instruction) | Not required | Not required |
| Station number | 0 | 1 |
| Mode Switch | Not available | Not available |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Cnet Dedicated Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-5-4. Communication Parameter

6-5-4-1. Station 0 (Master)

1) Double click ‘communication parameter’ in the parameter menu.

2) Set basic parameters (Baudrate, Station No. Parity, Data bit, Stop bit )

3) Click ‘LIST’ button in the dedicated menu.

4) Click the first line and edit send parameter

5) Click the second line and edit receive parameter

6) Connect and download parameter

7) Click ‘Link Enable’ in the on-line menu

6-5-4-2. Station 1 (Slave)

1) Double click ‘communication parameter’ in the parameter menu.

2) Set basic parameters (Baudrate, Station No. Parity, Data bit, Stop bit )

3) Connect and download parameter

4) Click ‘Link Enable’ in the on-line menu

6-6 User defined protocol service (GM6 / K200S ( Mitsubishi PLC)

6-6-1. Example Overview

By using ‘User defined protocol service’, GM6 / K200S reads data memory of Mitsubishi Melsec

A2U (D000 ~ D002, 3words)

6-6-2. System Configuration

6-6-3. Test Environment

|  | K200S | Mitsubishi |
| --- | --- | --- |
| CPU | GM6 CPU / K200S CPU | A2U CPU |
| Communication Module | G6L-CUEA (Slot 5) | AJ71UC24 |
| Cable | RS-422 | RS-422 |
| Programming (Instruction) | SND / RCV | Not required |
| Station number | 0 | 1 |
| Mode Switch | 0 (RS-422 User defined) | 5 (RS-422 Dedicated) |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Cnet User defined Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-6-4. Setting Cnet Basic Parameter

6-6-5. Communication Frame Editing

- AJ71UC24’s (MELSEC Serial communication module) Protocol frame (Command/Response format)

can be easily created by frame editor tool and that frame will be used with instruction in PLC program.

- AJ71UC24’s request(command) and response format is as below

1) Request Format (Cnet module ( AJ71UC24) : ASCII Code

2) Response Format (AJ71UC24 ( Cnet module) : ASCII Code

6-6-5-1. Send Frame editing

♧Point !

Command / Response Frame can be divided as some segment by frame editor.

User need to optimize frame structure by this segmentation, Some parts as constant string,

the other parts as variable.

For example, two cases below has a same result.

Case 1 (All constant string)                 Case 2 (Constant string + Variable)

6-6-5-2. Receive Frame editing

6-6-6. PLC Programming (for GLOFA)

Receive complete flag

- If the frame agreed with the frame downloaded to Cnet module is received, Cnet modules lets

the flag ‘ON’ Indicating that the receiving is completed successfully

| Flag Name | Item | Description |
| --- | --- | --- |
| _RCVn_232[ i ] _RCVn_422[ i ] | n (0~7) | Select slot number of Cnet |
|  | 232 | RS-232C |
|  | 422 | RS-422 / 485 |
|  | i | Entry number of receive frame designated by frame editor. |

6-6-7. PLC Programming (for Master K)

① Store the name of send frame in D000 ~ D007 as ASCII Code (8words)

| D007 | D006 | D005 | D004 | D003 | D002 | D001 | D000 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Q H51 | E H45 | R H52 |

② [ SND  H0105  D000  D0020  H0000  M010 ]

- H0105 : Channel & slot no. (01 = RS-422, 05 = slot no.)

- D0000 : Frame name set by frame editor (‘REQ’)

- D0020 : Start address of sending data to ‘SD1.’ designated by frame editor.

In this case, there is not ‘SD1.’ field in the frame (all constant string). So this device becomes

Dummy area.

- H0000 : Byte number of sending data to ‘SD1.’ Designated by frame editor

In this case, there is not ‘SD1.’ field in the frame (all constant string). So this value becomes

0 (zero)

- M010 : Communication status (M0100 ~ M010F)

| Error Code (M108 ~ M10F, 8bits) | Not Used (M102 ~ M107, 6bits) | M101 | M100 |
| --- | --- | --- | --- |

③ Store the name of receive frame in D010 ~ D017 as ASCII Code (8words)

| D017 | D016 | D015 | D014 | D013 | D012 | D011 | D010 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S H53 | E H45 | R H52 |

④ [ RCV H0105  D0010  D0200  D0300  M020 ]

- H0105 : Channel & slot no. (01 = RS-422, 05 = slot no.)

- D0010 : Frame name set by frame editor (‘RES’)

- D0200 : Start address of receiving data from ‘RD1.’ designated by frame editor.

- HD300 : Byte number of data received from ‘RD1.’ Designated by frame editor )

- M020 : Communication status (M0200 ~ M020F)

| Error Code (M208 ~ M20F, 8bits) | Not Used (M202 ~ M207, 6bits) | M201 | M200 |
| --- | --- | --- | --- |

⑤ Receive Flag (L0441) : Turns on per 1scan automatically when the frame is received

- This flag is a kind of special relay. User can not change value & address of this flag.

| Slot (Cnet) | Channel | Frame No. | Receive Flag |
| --- | --- | --- | --- |
| 0 Slot (L0000 ~ L007F) | RS-232C (L0000 ~ L003F) | Frame No.0 | L0000 |
|  |  | Frame No.1 | L0001 |
|  |  | Frame No.2 | L0002 |
|  |  | Frame No.63 | L003F |
|  | RS-422/485 (L0040 ~ L007F) | Frame No.0 | L0040 |
|  |  | Frame No.1 | L0041 |
|  |  | Frame No.2 | L0042 |
|  |  | Frame No.63 | L007F |
| 1 Slot (L0080 ~ L015F) | RS-232C (L0080 ~ L011F) |  |  |
|  | RS-422/485 (L0120 ~ L015F) |  |  |
| 5 Slot (L0080 ~ L015F) | RS-232C (L0400 ~ L043F) |  |  |
|  | RS-422/485 (L0440 ~ L047F) | Frame No.0 | L0440 |
|  |  | Frame No.1 | L0441 |
|  |  | Frame No.2 | L0442 |
|  |  | Frame No.63 | L047F |

6-7 User defined service (GM7 ( Mitsubishi PLC)

6-7-1. Example Overview

By using ‘User defined protocol service’, GM7 reads data memory of Mitsubishi Melsec

A2U (D000 ~ D002, 3words)

6-7-2. System Configuration

6-7-3. Test Environment

|  | GM7 | Mitsubishi |
| --- | --- | --- |
| CPU | GM7 CPU | A2U CPU |
| Communication Module | G7L-CUEC | AJ71UC24 |
| Cable | RS-422 | RS-422 |
| Programming (Instruction) | SND_MSG | Not required |
| Station number | 0 | 1 |
| Mode Switch | Selected by parameter | 5 (RS-422 Dedicated) |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Cnet User defined Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-7-4. Communication parameter setting

1) Double Click ‘Communication Parameter’ in the parameter menu.

- Click the ‘List’ button for Frame editing

- Send (Request) frame editing

4) Receive (Response) frame editing

6-7-5. Programming

6-7-6. Link Enabling

1) Connect and download parameter and program

2) Click ‘Link Enable’ in the on-line menu

6-8 Library service / Modbus (K200S / GM6 ( IBM PC)

6-8-1. Example Overview

By using Modbus protocol, IBM PC reads/write data memory In the PLC CPU and displays

results on the monitor screen.

6-8-2. System Configuration

6-8-3. Test Environment

|  | Computer | K200S / GM6 |
| --- | --- | --- |
| CPU | Pentium 133 | K200S / GM6 CPU |
| Communication Module | COM1 Port | G6L-CUEA |
| Cable | RS-232C | RS-232C |
| O/S | Windows98 | - |
| Development Language | MS Visual Basic | - |
| Station number | - | 1 |
| Mode Switch | - | 9 (On line switching mode) |
| Client / Server | Client (Master) | Server (Slave) |
| Communication Service | Modbus RTU Protocol Service |
| RS-232C Spec. | 9600bps, Data 8bit, Stop 1bit, None pariry |

6-8-4. Setting Cnet Basic Parameter

6-8-5. Writing library (Modbus driver) to flash memory

- Set the Cnet module to ‘Flash memory write mode’(Mode 8) with the mode selection switch.

- RUN LED of Cnet module will blink with 1 second period

- Run the frame editor and connect to the Cnet module.

- Select ‘modbus6.lib’(Modbus driver for GM6/K200S) in Open Lib menu

- select Online – Flash Memory – Write in the menu, then type the slot number at which the Cnet

module is mounted, and press ‘Write’ button.

- Set the Cnet module to ‘On-line mode’(Mode 9) with the mode selection switch and cycle Cnet

Module power.

- Run the frame editor and connect to the Cnet module, then select ‘Library mode’ in on line change

Menu.

6-8-6. Address Map

1) GM1/2/3/4/6 (K1000S/300S/200S)

- Modbus device (Modicon PLC Device) can be corresponded to the M(%M) area only.

- In case of bit device, M0000 ~ M0007 (%M0 ~ %M7) can not be correspond to Modicon Address.

- In case of word device, M000 (%MW0) can not be correspond to Modicon Address.

| Bit / Word | Modicon Address | GLOFA Address | Master K Address | Remarks |
| --- | --- | --- | --- | --- |
| Bit | □ 0008 | %M8 | M 0008 | Raead / Write |
|  | □ 0009 | %M9 | M 0009 |  |
|  | □ 0010 | %M10 | M 000A |  |
|  | □ 0011 | %M11 | M 000B |  |
|  | □ 0012 | %M12 | M 000C |  |
|  | □ 3071 | %M3071 | M 191F |  |
|  | □ 3072 | %M3072 | Not available |  |
|  | □ 9999 | %M9999 |  |  |
| Word | ■ 0001 | %MW1 | M 001 | Read / Write |
|  | ■ 0002 | %MW2 | M 002 |  |
|  | ■ 0003 | %MW3 | M 003 |  |
|  | ■ 0004 | %MW4 | M 004 |  |
|  | ■ 0005 | %MW5 | M 005 |  |
|  | ■ 0006 | %MW6 | M 006 |  |
|  | ■ 0191 | %M191 | M 191 |  |
|  |  |  | Not available |  |
|  | ■ 4999 | %MW4999 |  |  |
|  | ■ 5000 | Not available |  |  |
|  | ■ 9999 |  |  |  |

□: Identifier of Modicon device ( 0=Input, 1=Coil )

■: Identifier of Modicon device ( 3=Input register, 4=Holding register )

2) GM7 (K80S)

- In case of K80S, Modbus device (Modicon PLC Device) can be corresponded to all type & range of

device memory.

- In case of GM7, Modbus device (Modicon PLC Device) can be corresponded to %M area only.

| Bit / Word | Modicon Head Address | GLOFA Head Address | Master K Head Address | Remarks |
| --- | --- | --- | --- | --- |
| Bit | □ 0001 ~ | %M000 ~ | P 0000 ~ | Raead / Write |
|  | □ 4097 ~ | %M4096 ~ | M 0000 ~ |  |
|  | □ 8193 ~ | %M8192 ~ | L 0000 ~ |  |
|  | □ 12289 ~ | Not available | K 0000 ~ |  |
|  | □ 16385 ~ |  | F 0000 ~ |  |
|  | □ 20481 ~ |  | T 0000 ~ |  |
|  | □ 24577 ~ |  | C 0000 ~ |  |
| Word | ■ 0001 ~ | %MW0 ~ | P 000 ~ | Read / Write |
|  | ■ 4097 ~ | Not available | M 000 ~ |  |
|  | ■ 8193 ~ |  | L 000 ~ |  |
|  | ■ 12289 ~ |  | K 000 ~ |  |
|  | ■ 16385 ~ |  | F 000 ~ |  |
|  | ■ 20481 ~ |  | T 000 ~ |  |
|  | ■ 24577 ~ |  | C 000 ~ |  |
|  | ■ 28673 ~ |  | S 000 ~ |  |
|  | ■ 32769 ~ |  | D 000 ~ |  |

□: Identifier of Modicon device ( 0=Input, 1=Coil )

■: Identifier of Modicon device ( 3=Input register, 4=Holding register )

6-8-7. Computer Application Software (Modbus simulator)

- Run modbus.exe

2) Click ‘configuration’ on menu bar

3) Click ‘ON’ on menu bar (Communication is started)

4) Select ‘Display – Coils’ on menu bar

5) Select ‘Display – Input register’ on menu bar

# Text boxes

RUN/BPS

TX/BPS

RX/BPS

ACK/DATA-BIT

NAK/PARITY

ERR/EVEN-ODD

RS-485/STOP-BIT

SYS-RUN

Recive Frame name designated in frame editor

This value is string type, so ‘ must be attached

(‘RES‘)

0

RS-422

RS-232C

FG

SG

SDB

SDA

1

♣Point !

1.In the interlocking mode, the RS-232C channel operates as main channel and the RS-422

channel operates as the data path. The data structure of RS-422 channel is set as that of

RS-232C channel.

2.In stand-alone mode, RS-232C and RS-422 channel can operates in different operation modes.

TXD

0

1

2

3

4

8

9

7

6

5

RS-

232C

Internal

Memory

GM/MKS

CPU

CUEA

Communication

Processor

Data

Memory

COMM

①Command(Request)

④Response

Application

User Program

(Visual C++,

MMI Package)

②

③Access

Datas

requested

2

RS-

422

1

CUEA

GM/MKS

CPU

RS-

422

External Device

RS-

232C

Internal

Memory

0

②Requested(Command)

COMM

③Response

Application

User Program

①Request

④Response

Function Block

[ SND ]

Function Block

[ RCV ]

COMM

SND_MSG

RCV_MSG

Down Loading Cnet Parameter

Down Loading Ladder Program

& Cycle the power of Cnet module

# User Defined Service

2. Communication Frame

Editing

2. Library Selecting

### Library Service

(AB DF1 / MODUBUS)

# Dedicated Service

1. Basic Parameter Setting

|  | I/O |  | Description |
| --- | --- | --- | --- |
| Input | REQ | BOOL | Function block begins in rising edge (0( 1) |
|  | SLOT_NO | USINT | Cnet slot no. of self station |
|  | CH | UDINT | Communication channel select ( 0 : RS232C / 1 : RS422 ) |
|  | ST_NO | UDINT | Station no. of other PLC to communicate with function block (0~31) |
|  | VAR | STRING | Memory area of other PLC station to write or read data using function block. Input type should be string using ‘ ‘. And direct variables as byte type. ex) ‘%MB100’, ‘%QB20’, ‘%IB50’….. |
|  | DATA_LEN | USINT | Length of data(byte unit) to read/write (Max. 110 bytes) |
|  | DATA_WR | USINT ARRAY | Start address of Local PLC which has data to be written to other PLC (defines Direct variable as byte type) |
|  | DATA_RD | USINT ARRAY | Start address of Local PLC to save read data from other PLC (defines Direct variable as byte type ) |
| Output | NDR | BOOL | When this function operates properly, it will be On and keep On condition until next function block’s call. |
|  | ERR | BOOL | When the result of this function does not operate well, it will be On and keep On condition until next function block’s call. |
|  | STATUS | USINT | ERR : 1 ( error code, NDR : 1 ( ‘0’ |

3. Making the program

by using Function Block

& Frame file

1. Basic Parameter Setting

RS-232C Interface

IBM Compatible

Computer

D100

D101

Response

Command

P001 (P010~P01F)

P002 (P020~P02F)

K200S CPU &

G6L-CUEA

K200S CPU &

G6L-CUEA

RS-232C Interface

GM6 CPU & G6L-CUEA

K200S CPU & G6L-CUEA

ETX

Tail

1 Byte

K200S CPU & G6L-CUEC

GM6 CPU & G6L-CUEA

Command

%IQ0.0.0

A2U CPU / AJ71UC24

Response

D200 / RCV_DATA(0~1)

D201 / RCV_DATA(2~3)

D202 / RCV_DATA(4~6)

D000

D001

D002

Response

Command

D000 ~ D002

90AB

Data

2 Byte

5678

Data

2 Byte

1234

Data

2 Byte

01

Station

Number

2 Byte

STX

Header

1 Byte

FF

Self

Station

2 Byte

ENQ

Header

1 Byte

%QW0.0.0

%IW0.0.0

03

Number

2 Byte

0

Waiting

Time

1 Byte

Response

D0000

Head

Address

5 Byte

WR

Command

(Word

read)

2 Byte

FF

Self

Station

2 Byte

01

Station

Number

2 Byte

Command

RS-232C Interface

RS-422/485 Interface

GLOFA/ MKS PLC

(GM7 / K80S)

GLOFA/ MKS PLC

(GM7 / K80S)

Fixed area

Variable area : 6 Bytes

In the unit

Of Byte

Frame name will be used in instruction (SND)

SD1. Is fixed name

User can not change this Name

In case of GLOFA : SD1

In case of MKS : SD1.

## H03

SD1.

Moved by Ladder Program

In the unit

Of Byte

Frame name will be used in instruction (SND)

FF

Self

Station

2 Byte

ETX

Tail

1 Byte

90AB

Data

2 Byte

Done bit (Turns on during 1scan when instruction is executed normally)

5678

Data

2 Byte

Error bit (Turns on when an error occurs during communication)

1234

Data

2 Byte

01

Station

Number

2 Byte

STX

Header

1 Byte

Done bit (Turns on during 1scan when instruction is executed normally)

Error bit (Turns on when an error occurs during communication)

④

⑤

③

①

②

RDB

RDA

DISPLAY

RS-422

RUN/BPS

TX/BPS

RX/BPS

ACK/DATA-BIT

NAK/PARITY

ERR/EVEN-ODD

MODEM/STOP-BIT

SYS-RUN

RS-232C

MODE

G3L-CUEA

⑤

④

③

②

①

| No. | Name | Contents |
| --- | --- | --- |
| ① | LED displaying section | Indication of operating status of G3L-CUEA |
| ② | Display switch | Switch for indication of parameter and station number |
| ③ | Mode switch | Setting of operation Mode |
| ④ | Connector RS-232C | Connector RS-232C for connection with external devices |
| ⑤ | Connector RS-422/485 | Connector RS-422/485 for connection with external devices |

RUN/BPS

TX/BPS

RX/BPS

ACK/DATA

NAK/PARITY

ERR/EVEN-ODD

RS-485/STOP

SYS-RUN

RUN/BPS

TX/BPS

RX/BPS

ACK/DATA

NAK/PARITY

ERR/EVEN-ODD

MODEM/STOP

SYS-RUN

FG

SG

SDB

SDA

RDB

RDA

RS422

RS-232C

DISPLAY

RS-232C

RS-422

MODE

G4L-CUEA

①

⑤

②

④

③

| No. | Name | Contents |
| --- | --- | --- |
| ① | LED displaying section | Indication of operating status of G4L-CUEA |
| ② | Display switch | Switch for indication of parameter and station number |
| ③ | Mode switch | Setting of operation mode |
| ④ | Connector RS-232C | Connector RS-232C for connection with external devices |
| ⑤ | Connector RS-422/485 | Connector RS-422/485 for connection with external devices |

RS-232C

RUN	NAK

TX 	COM-ERROR

RX 	MODEM

ACK	SYS-RUN/ERR

G6L-CUEB

MODE

| No | Name | Contents |
| --- | --- | --- |
| ① | LED displaying section | Indication of operating status of G6L-CUEB |
| ② | Mode switch | Setting of operation mode |
| ③ | Connector RS-232C | Connector RS-232C for connection with external devices |

①

③

②

RUN	NAK

TX	COM-ERROR

RX	RS-485

ACK	SYS-RUN/ERR

G6L-CUEC

MODE

FG

RDB

RDA

SDB

SG

SDA

RS-422/485

| No | Name | Contents |
| --- | --- | --- |
| ① | LED displaying section | Indication of operating status of G6L-CUEC |
| ② | Mode switch | Setting of operation mode |
| ③ | Connector RS-422/485 | Connector RS-232C for connection with external devices |

①

③

②

①

⑤

②

④

③

2

3

4

8

9

7

6

5

RXD

PWR

GLOFA

###### G7L-CUEC

PROGRAMMABLE

LOGIC

CONTROLLER

③

①

②

External Device

(IBM Compatible PC

& Others)

RS-232C Interface

RS-232C Interface

RS-232C

Public telephone line

MODEM

MODEM

RS-232C

GLOFA/ MKS PLC

(G3L-CUEA/G4L-CUEA/

G6L-CUEA)

External Device

(IBM Compatible PC)

External Device

(IBM Compatible PC

& Others)

External Device

(IBM Compatible PC

& Others)

GLOFA/ MKS PLC

(GM6 / K200S)

GLOFA/ MKS PLC

(GM7 / K80S)

GLOFA/ MKS PLC

(GM7 / K80S)

External Device

(IBM Compatible PC)

MODEM

MODEM

GLOFA/ MKS PLC

(GM7 / K80S)

GLOFA/ MKS PLC

(GM6 / K200S)

PMU

PMU

RS-422/485 Interface

GLOFA/ MKS PLC

(GM7 / K80S)

GLOFA/ MKS PLC

(GM7 / K80S)

RS-422/485 Interface

External Device

(IBM Compatible PC

& Others)

GM7 / K80S

(G7L-CUEC)

GLOFA/ MKS PLC

(G3L-CUEA/G4L-CUEA/

G6L-CUEA)

GLOFA/ MKS PLC

(G3L-CUEA/G4L-CUEA/

G6L-CUEA)

External Device

(IBM Compatible PC

& Others)

♣Point !

When communicate via RS-422 or RS-485 channel, terminal resistors should be added at the ends of network wiring. The terminal resistor prevents a distortion of signal caused from reflected wave of cable. The terminal resistor should have the same resistance with the characteristic impedance of cable. If you use the recommended cable or equivalent, please connect two 120(, 1/2W resistors at the ends of network.

RS-422/485 Interface

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

RS-422/485 Interface

Station N

Station 1

Station 0

External Device

(IBM Compatible PC

& Others)

Station 0

External Device

(IBM Compatible PC

& Others)

·

·

SG

·

TXB

TXA

RXB

RXA

RS-422/485 Interface

·

SG

·

TXB

TXA

RXB

RXA

SG

·

TXB

TXA

RXB

RXA

·

SG

·

TXB

TXA

RXB

RXA

Station 1

Station N

Station N

Station 1

Station 0

External Device

(IBM Compatible PC

& Others)

RS-422/485 Interface

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

GM7 / K80S

(G7L-CUEC)

External Device

(IBM Compatible PC

& Others)

Station N

Station 1

Station 0

Station 2

Station 1

Station 2

Station N

·

SG

·

TXB

TXA

RXB

RXA

·

SG

·

TXB

TXA

RXB

RXA

·

SG

·

TXB

TXA

RXB

RXA

Device Address number

Data type (X,B,W,D)

Device type

Start of data

·

SG

·

TXB

TXA

RXB

RXA

·

SG

·

TXB

TXA

RXB

RXA

·

SG

·

TXB

TXA

RXB

RXA

·

SG

·

TXB

TXA

RXB

RXA

3

·

SG

·

TXB

TXA

RXB

RXA

W

M

%

♣Point !

- The CPU doesn’t care capital or small letter in frame except main command. For example,

‘%MW100’ and ‘%mw100’ have same meaning. However, if the main command is written in small

letter, the BCC check will be executed.

- When read or write a bit, the last digit of address should be a capital letter.

Example)	%mx001f		( X )

%mx001F	( O )

- In the above examples, device numbers are consist of 4 digits and it is the recommended

format of MASTER-K series. However, 2 ~ 8 digits are allowed to express a device number.

Example) %MX01 = %MX001 =  …  = %MX0000001 = %MX00000001

%DW31 = %DW031 =  …  = %DW0000031 = %DW00000031

| Format name | Header | Station number | Command | type | Length of device definition | Head Device To be accessed | Number of data | Tail | Frame check |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frame example | ENQ | h10 | R (r) | SB | h06 | %MW100 | h02 | EOT | BCC |
| ASCII value | h05 | h3130 | h52 (h72) | h5342 | h3036 | h254D57313030 | h3032 | h04 |  |

Structured Data Area

| Format name | Header | Station number | Command | type | Block * Number | Number of data | Data | Tail | Frame check |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frame example | ACK | h10 | R (r) | SB | 01 | h04 | h12345678 | ETX | BCC |
| ASCII value | h06 | h3130 | h52 (h72) | h5342 | H3031 | h3034 | h3132333435363738 | h03 |  |

Structured Data Area

| Format name | Header | Station number | Command | type | Error code (Hex 2 byte) | Tail | Frame check |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Frame example | NAK | h10 | R (r) | SB | h2232 | ETX | BCC |
| ASCII value | h15 | h3130 | h52 (h72) | h5342 | h32323332 | h03 |  |

SND  sl  Fnam  snd  n  SS

C  D

A  B

C  D

RCV  sl  Fnam  rcv  n  SS

A  B

Network

Network

GM_RD : This function block is used for reading data

of other station.

GM_WR : This function block is used for writing data

of other station.

READ : This instruction is used

for reading data of other station.

WRITE : This instruction is used

for writing data of other station.

READ  sl   st  D  S  n  SS

WRITE  sl   st  D  S  n  SS

2. Making the program

by using Function Block

or Instruction (Only for

Communication between

Cnet modules)

GM_WR

GM_RD

Writing Lib. to

Flash Memory

4. Mode selecting by using

rotary switch of Cnet module

4. Mode selecting by using

rotary switch of Cnet module

0

1

2

3

4

8

9

7

6

5

0

1

2

3

4

8

9

7

6

5

3. Mode selecting by using

Cnet frame editor (On line

Mode switching)

Data Value (2words)

Station 0 (Master)

Station 1 (Slave)

1. Basic Parameter Setting

Head address of

Master(self) station

Head address of

Slave station

Slave station no.

to be accessed

Head address of

Master(self) station

Head address of

Slave station

Slave station no.

to be accessed

%IW0.0.0

Comm. status

Number of word to be read : 2

Master(self) station’s head area to be stored : D100

Slave station’s head area to be read : P001 (P010~P01F)

Channel & Station No. of slave

Slot No. : 5

Channel (2words) : 0 (RS-232C)

Station No. of slave (2words) : 1

Down Loading Cnet Parameter

Down Loading Cnet Parameter

K200S / GM6 CPU

& G6L-CUEA

IBM Compatible

Computer

Command

Response

RS-232C Interface

Frame editing is not rquired

Modbus Station No.

Slave station No. (Station No. of Cnet)

Protocol (RTU), Buadrate (9600bps), Parity (None)

Head address(word) to be read and number

- M002 ~ M006 (%MW2 ~ %MW6)

Head address(Bit) to be read and number

- M0008 ~ M0017 (%M8 ~ %M23)

M0008 is ON

M000A is ON

M000B is ON

M000D is ON

M000F is ON

Value of M002(word) is 1234

Note !!!

In case of GLOFA : RD1

In case of MKS : RD1.

Send Frame name designated in frame editor.

This value is string type, so ‘ must be attached

(‘REQ‘)

Array variable(USINT type) in which received

data is stored.

(this array must have more than 6 component

to store 3 words)

In this example, this area is not required.

But this area must be filled by dummy variable.

A2U CPU / AJ71UC24

GM7 & G7L-CUEC

Command

Response

RS-422/485 Interface

%MB0~%MB1

%MB2~%MB3

%MB4~%MB5

D000

D001

D002

Buadrate (9600bps)

Parity (None)

Data (8bit), Stop(1bit)

User Defined

Master mode

ENQ

Header

1 Byte

D000 ~ D002

03

Number

2 Byte

0

Waiting

Time

1 Byte

D0000

Head

Address

5 Byte

WR

Command

(Word

read)

2 Byte

FF

Self

Station

2 Byte

01

Station

Number

2 Byte

Maximum character of

Each constant area is

10 character.

Fixed area

Variable area : 6 Bytes

ETX

Tail

1 Byte

FF

Self

Station

2 Byte

90AB

Data

(D002)

2 Byte

5678

Data

(D001)

2 Byte

1234

Data

(D000)

2 Byte

01

Station

Number

2 Byte

STX

Header

1 Byte

%MB4 = 16#90

%MB5 = 16#AB

%MB2 = 16#56

%MB3 = 16#78

%MB0 = 16#12

%MB1 = 16#34

Send frame entry number designated by comm. parameter

“Built-in Cnet” Dip switch should be ‘ON’

External Device

(IBM Compatible PC

& Others)

GLOFA/ MKS PLC

(GM7 / K80S)

Connection#1 (RS232C/Cnet)

Connection#2 (RS232C/Loader)

Loader(GMWIN/KGLWIN) or

Touch Screen(PMU)

“Built-in Cnet” Dip switch should be ‘OFF’

External Device

(IBM Compatible PC

& Others)

Connection#2 (RS232C/Loader)

Connection#1 (RS232C/Cnet)

GM7 / K80S

(G7L-CUEB)

Loader(GMWIN/KGLWIN) or

Touch Screen(PMU)

Command

Station 1 (Slave)

Station 0 (Master)

Response

RS-232C Interface

GM6 CPU &

G6L-CUEA

GM6 CPU &

G6L-CUEA

%MB100

%MB101

%MB102

%MB103

Data Value (2words)

%MB0

%MB1

%MB2

%MB3