1.Features

- GLOFA DeviceNet module (G4L-DUEA, G6L-DUEA, GOL-DSQA, GOL-DSIA)

supports ODVA (Open DeviceNet Vendor Association) standard specification.

- Max. 63 slave station (Max 2048 points) can be controlled 1 master module.

- Station no(Mac Address) and transmission speed (baudrate) can be selected

by switch on module

- Various slave that provided by other maker can be connected to GLOFA DeviceNet

master module (G4L-DUEA / G6L-DUEA)

- Digital I/O

- Actuator

- Limit Switch

- Photo Sensor

- Inverter

- Position Controller

- A/D, D/A Converter

- GLOFA DeviceNet slave module (GOL-DSQA, GOL-DSIA) can be connected to

master module that provided by other maker

- Max. 2 master module can be installed in main base

# Caution

GLOFA DeiveNet system requires …..

- GLOFA GMWin : Ver. 3.3 or higher

- GLOFA GM4 CPU : Ver 2.3 or higher

- GLOFA GM6 CPU : Ver 1.3 or higher

2. Specification

2-1 Performance Specification

|  | Description |
| --- | --- |
| Topology | Linear Bus (Power & Signal on the same network cable) |
| Max. no of station | 64 station |
| No. of points | Max. 2048 points / slave |
|  | Max. 2048 points / master module |

| Transmission Speed | Distance (Thick / Thin cable) | Drop length |  |
| --- | --- | --- | --- |
|  |  | 1 drop | Cumulative |
| 125 kbps | 500 / 100m | 6m | 156m |
| 250 kbps | 250 / 100m | 6m | 78m |
| 500 kbps | 125 / 100m | 6m | 39m |

3. System Configuration

3-1. In case that GLOFA works as master

## GMWIN

GM 4 (Master)

# OUT

# DeviceNet

# CPU

# PWR

GM 6 (Slave)

# OUT

# DeviceNet

# CPU

# PWR

PMU

# IN

# IN

DeviceNet

OMRON

AB

Other maker’s I/O module

Inverter

GLOFA I/O module

3-2. In case that GLOFA works as slave

DeviceNet

Configurator

## GMWIN

GM 4 (Slave)

GM 6 (Slave)

AB, OMRON PLC (Master)

# OUT

# DeviceNet

# CPU

# PWR

# OUT

# DeviceNet

# CPU

# PWR

# OUT

# DeviceNet

# CPU

# PWR

# IN

# IN

# IN

DeviceNet

OMRON

AB

Other maker’s I/O module

GLOFA I/O module

Inverter

4. Name of Parts

4-1. G4L-DUEA

G4L-DUEA

MODE

ADDRESS

10

1

G4L-DUEA

MS

NS

| LED Display |  |
| --- | --- |
| 7-Seg. | Display status of module |

| LED Lamp |  |
| --- | --- |
| MS | Display I/F status of module |
| NS | Display network status of module |

Station no. setting switch

Mode setting switch (Baudrate, Master/Slave)

Connector

4-2. G6L-DUEA

MS NS

G6L-DUEA

MODE

## ADDRESS

### 10

### 1

G6L-DUEA

| LED Lamp |  |
| --- | --- |
| MS | Display I/F status of module |
| NS | Display network status of module |

Station no. setting switch

Mode setting switch (Baudrate, Master/Slave)

Connector

※Mode Setting

| Module | Switch | Setting |  | Master / Slave |  |
| --- | --- | --- | --- | --- | --- |
|  |  | SW1 | SW2 |  |  |
| 4 3 2 1 ON G4L-DUEA G6L-DUEA |  | OFF | OFF | Master |  |
|  |  | ON | OFF | Slave (Server) |  |

| Module | Switch | Setting |  | Baudrate |  |
| --- | --- | --- | --- | --- | --- |
|  |  | SW3 | SW4 |  |  |
| 4 3 2 1 ON G4L-DUEA G6L-DUEA |  | OFF | OFF | 125 kbps |  |
|  |  | ON | OFF | 250 kbps |  |
|  |  | OFF | ON | 500 kbps |  |
|  |  | ON | ON |  |  |

4-3. G0L-DSQA



x 1

PWR

NS

MODE

On

Off

ADDRESS

MS

NC   0     1      2     3

COM1  4     5     6     7   COM2

NC   8     9    10    11

COM3  12    13    14    15

COM4

24V

24G

INPUT

DC 24V

              



x 10

G0L-DSQA

|  Station no. switch | 0 ~ 63 (Decimal display) |
| --- | --- |
| ×10 | 10 unit |
| ×1 | 1 unit |
|  LED Display | Communication status display |
| PWR | Power status |
| MS | Interface status |
| NS | Network status |
|  Mode switch | Baudrate setting |
| 1:Off 2:Off | 125 kbyte |
| 1:On 2:Off | 250 kbyte |
| 1:On/Off 2:On | 500 kbyte |
|  LED Display | Out put display |
| G0L-DSQA | 16points |

|  Connector | 5-PIN connector |
| --- | --- |
| CON1 | DeviceNet connector |

|  Terminal Block |  |  |
| --- | --- | --- |
| G0L-DSQA | 0 ~ 15 | Output terminal block |
|  | COM1 ~ COM4 | Common (4Point Common) |
|  | NC |  |
|  | 24V | +24VDC IN |
|  | 24G | -24VDC IN |

4-4. G0L-DSIA



x 1

PWR

NS

MODE

On

Off

ADDRESS

MS

NC   0     2      4     6

COM1  8     10    12    14  COM2

NC   1     3     5    7

.      9    11    13    15

.

24V

24G

INPUT

DC 24V

              



x 10

G0L-DSIA

|  Station no. switch | 0 ~ 63 (Decimal display) |
| --- | --- |
| ×10 | 10 unit |
| ×1 | 1 unit |
|  LED Display | Communication status display |
| PWR | Power status |
| MS | Interface status |
| NS | Network status |
|  Mode switch | Baudrate setting |
| 1:Off 2:Off | 125 kbyte |
| 1:On 2:Off | 250 kbyte |
| 1:On/Off 2:On | 500 kbyte |
|  LED Display | Input display |
| G0L-DSQA | 16points |

|  Connector | 5-PIN connector |
| --- | --- |
| CON1 | DeviceNet connector |

|  Terminal Block |  |  |
| --- | --- | --- |
| G0L-DSQA | 0 ~ 15 | Input terminal block |
|  | COM1 ~ COM4 | Common (4Point Common) |
|  | NC |  |
|  | 24V | +24VDC IN |
|  | 24G | -24VDC IN |

5. Example

5-1. System Configuration

# IN

# DeviceNet

Out 16

Out 16

Ethernet

GM4 CPU

PWR

High speed link

Parameter

00 Station

(Master)

High speed link

Parameter

TAB (6 Port)

03 Station

(Slave)

# DeviceNet

Out 16

Out 16

GM6 CPU

PWR

# IN

G0L-DSQA

AB Flex I/O

(1794-ADN / 1794-0816 / 1794-1816)

01 Station

(Slave)

02 Station

(Slave)

5-2. Test Data Flow

# DeviceNet

Out 16

Out 16

Ethernet

GM4 CPU

PWR

00 Station

(Master)

# IN

%MW0

%MW2

%QW0.2.0

%MW1

%QW0.3.0

%QW0.1.0

%MW0

# DeviceNet

# IN

Out 16

Out 16

GM6 CPU

PWR

G0L-DSQA

01 Station

(Slave)

02 Station

(Slave)

03 Station

(Slave)

5-3 High Speed Link Parameter (Master Station / GM4)

Only

Available

Not support

yet

In the unit of Byte

Master → Slave 1 (Remote)

Master PLC’s Area

Slave 1 (Remote) → Master

Master PLC’s Area

In the unit of Byte

Master → Slave 2 (Remote)

Even if AB Flex I/O (1794-ADN / 1794-0816 / 1794-1816) has 16points input and output, this slave

module occupies 32points (4bytes) input and output.

5-4 High Speed Link Parameter (Slave Station / GM6)

In case of setting the parameter at slave station,

This station No. means Self station no. (Station no. of GM6)

Slave 1 (Remote) → Master