1. Specification

1.1 Perfomance Specification

| Item |  | Description |
| --- | --- | --- |
| Transmission Speed |  | 1Mbps |
| Encoding type |  | Manchester Biphase-L |
| Electric | Transmission Distance (Segment) | Max. 750m |
|  | Total Transmission Distance (Using Repeaters) | Max. 750m  (6 repeater + 1) = 5.25 km |
|  | Cable | Twisted pair shielded cable |
| Optical | Transmission Distance (Segment) | Max. 3km |
|  | Total Transmission Distance (Using EOC) | Max. 3km  (6 EOC +1) = 21km |
|  | Cable | Optical cable |
| Max. No. of Station |  | Master + slave = 64Station (1 Master, 63 Slave) |
| Access Method |  | Circulated token passing |

- ♣Note !

- Max. Transmission size per station

| Modules |  | Send + Receive per Station | Send per Station | No. of Block | Block | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Fnet Module | G3L-FUEA (K7F-FUEA) | 3840 words | 1920 words (32block  60word) | 64 blocks | 60 words |  |
|  | K3L-RBEA |  |  |  |  |  |
|  | G4L-FUEA (K4F-FUEA) |  |  |  |  |  |
|  | G6L-FUEA (K3F-FUEA) |  |  |  |  |  |
|  | G0L-FUEA |  |  |  |  |  |

1.2 Twisted pair cable for Fnet

| Cable contents |  |  |  |  |
| --- | --- | --- | --- | --- |
| Product name |  | Low Capacitance LAN Interface Cable |  |  |
| Type name |  | LIREV-AMESB |  |  |
| Size |  | 2  1.0mm (GS 92-3032, 18 AWG) |  |  |
| Maker |  | LG CABLE CO.,LTD |  |  |
| Electric characteristics |  |  |  |  |
| Item |  | Unit | Characteristic | Test Condition |
| Conductor resistance |  | /km | 21.8 or less | Normal Temp. |
| Withstanding voltage(DC) |  | V/min | Withstands at 500V for 1 minute | In air |
| Insulation resistance |  | MEGA -km | 1,000 or more | Normal Temp. |
| Static electricity capacity |  | pF/m | 45 or less | 1 kHz |
| Characteristic impedance |  |  | 120  12 | 10 MHz |
| Characteristics in appearance |  |  |  |  |
| Conductor | Number of core | CORE | 2 |  |
|  | Specification | AWG | 18 |  |
|  | Configuration | NO./mm | 1/1.0 |  |
|  | Outer diameter | mm | 1.0 |  |
| Insulator | Thickness | mm | 0.9 |  |
|  | Outer diameter | mm | 2.8 |  |

  Structural drawing

Conductor

Braided material

Sheath material

Insulator

AL/Mylar Tape

Ground line

1.3 Optical cable for Fnet

Type name :	G0C-F□□□ (□□□ is length of cable, unit : m)

Ex.) Optical cable 10m : G0C-F010

Specifications of optical cable

| Cable contents |  |
| --- | --- |
| Type name | Y22□□□□ : For indoor (for Bi-directional communication) D22□□□□ : For outdoor (for Bi-directional communication) |
| Connector type | ST - Type |
| Maker | Hewlett Packard(H.P) |

| Segment |  | For indoor(standard) | For outdoor(standard) |
| --- | --- | --- | --- |
|  |  | Y22□□□□ | D22□□□□ |
| Outer diameter (mm) |  | 2.9  5.8 | 4.8 |
| Min. Radius of curvature | Loaded (cm) | 5.0 | 7.5 |
|  | Unloaded (cm) | 3.0 | 4.8 |
| Weight(Kg/m) |  | 16 | 21 |

| Contents | Characteristic | Unit |
| --- | --- | --- |
| Core | 62.5 | m |
| Cladding | 125 | m |
| Max. attenuation | 5 | dB/km |
| Standard attenuation | 4.5 | dB/km |

Connector type

Connector type

Ex.) If the cable type is Y226969, connector type is ST and the

shape is stainless at both of the connectors.

  Outside drawing of optical cable

For indoor(Y22□□□□)

For outdoor(D22□□□□)

2. System Configuration

1) CPU Link system (Twisted pair cable)

|  | Devices for network A (Fnet electric) |  |  |  |
| --- | --- | --- | --- | --- |
|  | Type | Module name | Ex. of station number setting |  |
|  | FAM4.0 | G0L-FUEA | 0 |  |
|  | GM3 / K1000S | G3L-FUEA / K7F-FUEA | 1 |  |
|  | GM3 / K1000S | G3L-FUEA / K7F-FUEA | 2 |  |
|  | GM3 / K1000S | G3L-FUEA / K7F-FUEA | 3 |  |
|  | GM4 (GM6) K300S (K200S) | G4L-FUEA (G6L-FUEA) K4F-FUEA (K3F-FUEA) | 4 |  |
|  | PMU-500 | PM0-500F | 5 |  |

2) CPU Link system (Optical cable)

| Devices for network A (Fnet optical) |  |  |  |
| --- | --- | --- | --- |
| Type | Module name | Ex. of station number setting | Cable connection |
| K1000s / GM3 | G3L-FUOA / K7F-FUOA | 0 | TransmissionReceive (Active coupler) ReceiveTransmission (Active coupler) |
| K1000s / GM3 | G3L-FUOA / K7F-FUOA | 1 |  |
| K1000s / GM3 | G3L-FUOA / K7F-FUOA | 2 |  |
| Active coupler | G0L-FACA/FABA/FAPA | Not available |  |

3) Remote/slave Link system (Twisted pair cable)

|  | Devices for network A (Fnet electric) |  |  |  |
| --- | --- | --- | --- | --- |
|  | Type | Module name | Ex. of station number setting |  |
|  | GM3 K1000S | G3L-FUEA K7F-FUEA | 0(slot 0) |  |
|  | GM3 K1000S | G3L-FUEA K7F-FUEA | 2(slot 0) |  |

|  | Devices for network B (Fnet electric) |  |  |  |
| --- | --- | --- | --- | --- |
|  | Type | Module name | Ex. of station number setting |  |
|  | GM3 K1000S | G3L-FUEA K7F-FUEA | 1(slot 1) |  |
|  | GM3 remote I/O K1000S remote I/O | G3L-RBEA K7F-RBEA | 3 |  |
|  | GM4 remote I/O K300S remote I/O | G4L-RBEA K4F-RBEA | 4 |  |
|  | Stand-alone remote output | G0L-SMQA | 5 |  |

3. Interface Module

RUN

LAS

TOKEN

TX/RX   FAULT

K3F-FUEA

ON-LINE

TEST1

TEST2

CON1

①

②

③

④

⑤

×10

×1

CON2

①Type name indicating section

Indicates type name of communication module

| ②LED indicating section |  |
| --- | --- |
| RUN | Indicates the status of CPU module and interface |
| LAS | Indicates that communication module is performing LAS function. |
| TOKEN | Indicates whether communication module has a token or not. |
| Tx/Rx | Indicates whether communication module is transmitting/ receiving or not. |
| FAULT | Flickers when the error that normal operation is not possible occurred in communication module |

③Station number setting switch

Sets station number in the range of 0~63 station(Use decimal).

④Mode setting switch

Sets operation mode of communication module

⑤Communication connector

Connector for electric cable connection to connect communication module.

4. Example of CPU Link system

4.1 System configuration

Fnet (1Mbps, 64station, 750m, Twisted pair cable)

Station No. 0

Station No. 1

Station No. 2

Fnet-Module

G6L-FUEA

K3F-FUEA

4.2 Wiring

###### ST #1

###### ST #2

###### ST #0

Frame shield

6

6

7

7

Frame shield

Terminal resistance

(110Ω, 0.5W)

6

6

7

7

Terminal resistance

(110Ω, 0.5W)

4.3 Data flow

1) GLOFA GM6

00 Station

01 Station

02 Station

%IW0.0.0 (Block 0)

%MW50

(Block 0)

%IW0.0.1

(Block 0)

%QW0.1.0

%QW0.1.1

%QW0.1.0

%MW100

%QW0.1.0

Not

Defined

4.4 Setting Link Parameter (GLOFA GM6)

4.4-1 Link Parameter of Station 0

1) Connect GMWin to Station 0

2) Select ‘Link Parameter’ in parameter menu of GMWIN

Click here for

Setting a self-station

Select High Speed Link 1

(In case of using two Fnet module

in a main base, high speed link 1

and 2 will be set)

Select slot no. Fnet module

mounted and self station number

3) High Speed Link Parameter for sending (Station 0  All other station)

In case of CPU Link, Select Local

In case of Remote Link, Select Remote

Head addres to be sent

(%IW0.0.0 is sent to

all other stations)

In case that two or more

sending area is used,

Each sending must have a

different Block No..

♣ Point

- Block No

This is set to transmit and receive many data of several area from one station, and distinguishes data of many

block each other.

Station number and block number configured from transmission station is transmitted with transmission data.

Block number and station number should be set for all of Tx/Rx station.

Because storing the data in Receive Area can be made if the block No. is the same with other station No. of

high Speed link Receiving parameter.

Transmission block number can be set up to 32 and receive block number also can be set up to 32 for one

station, so max. of each Tx/Rx block number is limited to 34. In this time, the same block No. setting with

same station No. is impossible.

- Tx/Rx Period

High speed link executes transmission and receive at that time when PLC program is finished by the

parameter which user previously configured.

If scan time of PLC program is short(within several ms), communication module transmits data according to

program scan, and the increase of communication quantity with this causes reduction of communication efficiency.

To prevent this, user can set communication period from 20ms to 10sec.

Tx/Rx period means transmission period if selected block is set to transmission, and this means data receive

checking period of selected block if it is set to receive.

Transmission period determines data transmission period.

For example, if transmission data is set to 200ms(standard value), it will be transmitted every 200ms.

If scan time of PLC program is longer than transmission period previously set, it will be transmitted when program

scan is finished, and transmission period will be the same as scan time of PLC program.

4) High Speed Link Parameter for receiving (Station 1  Station 0/Self Station)

Head addres to be stored

(Data from station 1 is

stored in %QW0.1.0)

Other station’s no.

from which data is

received

Other station’s (St.1)

block no.

5) High Speed Link Parameter for receiving (Station 2  Station 0/Self Station)

Head addres to be stored

(Data from station 2 is

stored in %QW0.1.1)

Other station’s no.

from which data is

received

Other station’s (St.2)

block no.

4.4-2 Link Parameter of Station 1

1) Connect GMWin to Station 1

2) Select ‘Link Parameter’ in parameter menu of GMWin

Click here for

Setting a self-station

Select High Speed Link 1

(In case of using two Fnet module

in a main base, high speed link 1

and 2 will be set)

Select slot no. Fnet module

mounted and self station number

3) High Speed Link Parameter for sending (Station 1  All other station)

In case of CPU Link, Select Local

In case of Remote Link, Select Remote

Head addres to be sent

(%MW50 is sent to

all other stations)

In case that two or more

sending area is used,

Each sending must have a

different Block No..

4) High Speed Link Parameter for receiving (Station 0  Station 1/Self station)

Head addres to be stored

(Data from station 0 is

stored in %QW0.1.0)

Other station’s no.

from which data is

received

Other station’s (St.0)

block no.

5) High Speed Link Parameter for receiving (Station 2  Station 1/Self station)

Head addres to be stored

(Data from station 2 is

stored in %MW100)

Other station’s no.

from which data is

received

Other station’s (St.2)

block no.

4.4-3 Link Parameter of Station 2

1) Connect GMWin to Station 2

2) Select ‘Link Parameter’ in parameter menu of GMWin

Click here for

Setting a self-station

Select High Speed Link 1

(In case of using two Fnet module

in a main base, high speed link 1

and 2 will be set)

Select slot no. Fnet module

mounted and self station number

3) High Speed Link Parameter for sending (Station 2  All other station)

In case of CPU Link, Select Local

In case of Remote Link, Select Remote

Head addres to be sent

(%IW0.0.1 is sent to

all other stations)

In case that two or more

sending area is used,

Each sending must have a

different Block No..

4) High Speed Link Parameter for receiving (Station 0  Station 2/Self station)

Head addres to be stored

(Data from station 0 is

stored in %QW0.1.0)

Other station’s no.

from which data is

received

Other station’s (St.0)

block no.

4.4-4 Parameter Download & Link Enable

- After parameter writing, high speed link is maintained to the stop status.

- To start communication, user must set link enable for each station

- Link enable setting is possible in the stop mode only. and if high speed link enable setting is

started, high speed link is performed regardless of PLC operation mode

- Parameter and link enable information are preserved, even if power is off due to battery back-up

in PLC CPU.

| CPU Mode | Parameter downloading | Link enable setting | High speed link operation | Remark |
| --- | --- | --- | --- | --- |
| PLC RUN | × | × | ○ | Only if high speed link enable, it is operated. |
| PLC STOP | ○ | ○ | ○ |  |
| PLC PAUSE | × | × | ○ |  |
| PLC DEBUG | × | × | ○ |  |

- ‘Link Enable’ procedure is as belows

- Connect GMWin to the station 0

- Switch CPU mode to ‘STOP’

- Select ‘Online – Link enable’ in the memu

3) Set Link Enable for High Speed Link 1 (HS Link 1)

♣ Setting Link Parameter (for Master K)

- Operating and concept of Fnet system for Master K is the same as that of GLOFA

- Software(KGLWin) operation is different only for Link Parameter setting.

- Link parameter setting procedure is as below

1) Clink ‘Parameter’ in the project menu.

2) Select ‘Link 1’ (In case of using two Fnet module in a main base, Link 1 and 2 will be set)

Select slot no. Fnet module

mounted and self station number

Link Enable setting

3) Click the first link in link parameter setting window.

- In case of send (Sned data to all other stations)

In case that two or more sending area is used,

Each sending must have a different Block No..

Head addres to be sent

(P000 is sent to all other stations)

Send / Receive setting

- Local Out : Send to Local (CPU) station

- Local In : Receive from Local (CPU) station

- Remote Out : Send to Remote(I/O) station

- Remote In : Receive from Remote(I/O) station

- In case of receive (Receive data from one station designated)

In case that two or more sending area is used,

Each sending must have a different Block No..

Send / Receive setting

- Local Out : Send to Local (CPU) station

- Local In : Receive from Local (CPU) station

- Remote Out : Send to Remote(I/O) station

- Remote In : Receive from Remote(I/O) station

Head addres to be sent

(M000 is sent to all other stations)

5. Example of Remote Link System

5-1. System Configuration

Fnet (1Mbps, Max 750m, Twisted pair cable)

I

16

I

32

Q

16

Q

32

•••

I

32

Q

16

•••

Station No. 0 (Master)

Station No. 1 (Remote)

Station No. 2 (Remote)

Fnet Master Module

GLOFA : G3L-FUEA, G4L-FUEA, G6L-FUEA

Master K : K7F-FUEA, K4F-FUEA, K3F-FUEA

Fnet Slave Module

GLOFA : G3L-RBEA, G4L-RBEA, G6L-RBEA

Master K : K7F-RBEA, K4F-RBEA, K3F-RBEA

5-2. Example Data Flow

Station No. 0 (Master)

%MW4

~%MW5

%MW2

~%MW3

%MW1

%MW0

%IW0.6.0

~%IW0.6.1

%QW0.7.0

Block 0

Block 1

Block 2

Block 3

Block 4

Block 5

%QW0.3.0

~%QW0.3.1

%IW0.2.0

~%IW0.2.1

%QW0.1.0

%IW0.0.0

%IW0.0.0

~%IW0.0.1

%QW0.1.0

I

16

I

32

Q

16

Q

32

•••

Station No. 1 (Remote)

I

32

Q

16

•••

Station No. 2 (Remote)

5-3. Link Address Mapping (GLOFA)

|  | Station 1 |  |  |  | Station 2 |  |
| --- | --- | --- | --- | --- | --- | --- |
| Slot No. | 0 | 1 | 2 | 3 | 0 | 1 |
| In / Out | Input 16 | Output 16 | Input 32 | Output 32 | Input 32 | Output 16 |
| Block No. | 0 | 1 | 2 | 3 | 4 | 5 |
| Remote Address | %IW0.0.0 | %QW0.1.0 | %IW0.2.0 ~%IW0.2.1 | %QW0.3.0 ~%QW0.3.1 | %IW0.0.0 ~%IW0.0.1 | %QW0.1.0 |
| Master Address | %MW0 (%MX0 ~%MX15) | %MW1 (%MX16 ~%MX31) | %MW2 ~%MW3 (%MX32 ~%MX63) | %MW4 ~%MW5 (%MX64 ~%MX95) | %IW0.6.0 ~%IW0.6.1 | %QW0.7.0 |

- Remote address means just real in/out position and size then these address matched to

master address.

- When programming on master side for controlling remote I/O, master address matched remote

address will be used.

- In this example, slot 6 and 7 of master regard as being empty (not occupied by any module)

- Each sending and receiving should have a different block number.

5-4. Link Parameter (GLOFA)

- Setting for Station 1

Master Head Address

Remote Station

Input Head Address

Remote Station No.

Master Head Address

Remote Station

Output Head Address

- Setting for Station 2

Remote Station

Input Head Address

Master Head Address

(This area should be

not occupied by any

other module)

Master Head Address

(This area should be

not occupied by any

other module)

Remote Station

Output Head Address

3) Link Parameter setting completed

5-5. Downloading Link parameter and Link enable

1) Connect GMWin to GLOFA then download parameter.

2) Select ‘On line – Link Enable’ on the GMWin menu.

3) Select ‘HS Link 1’.