GETTING STARTED

MODBUS SIMULATOR (Mdbus) FOR WINDOWS 95/98/NT

Modicon, An AEG Company, Modicon Modbus Protocol Version

The program can be installed on any IBM or compatible PC equipped with a 386 or higher microprocessor.  The machine must be running Windows 95 or NT with at least one available serial communications port.  The 3 1/2 inch floppy contains an installation program which can invoked via the "Start - Run" option of the DeskTop Manager by typing either A:\setup or B:\setup in the open space as required.

For familiarization purposes, two instances of Mdbus can be run at the same time in the same machine and be made to communicate if two serial ports are available and TX and RX are crossed from one serial port to another.  One instance should be configured as a Master and the other as a Slave.  It is possible to invoke up to four instances of the program simultaneously if memory and serial ports are available.  The first instance of MDBUS is named MDBUS, the second - MDBUS0, the third MDBUS1, and the fourth - MDBUS2.

When the program is invoked for the first time, the Configuration Window will appear.  If the Ok button is pressed, the following conditions will apply.  The Mode will be MASTER (ie. will poll a Slave).  The Slave will be polled via communications port one at 1200 baud with no parity and RTU format.  The Slave polled will have an address of 1.  MDBUS will raise RTS for 55 milliseconds before any characters are transmitted (in case communications is via a 202 type modem or Radio link).  It will poll for 200 coil status starting at point 1 (index 0), 200 input status starting at point 1 (index 0), 30 input registers starting at register 1 (index 0), 100 holding registers starting at register 1 (index 0), and no floating point or long integer values.  Note that Mdbus takes the starting point number for each Data Type, subtracts 1, and uses this as the start register address in its poll requests.  It will attempt each poll three times if necessary for a successful response.  If the default configuration is not suitable, it can be modified.  Pressing the Help button will bring up the Windows Help Facility program.  Via the Search feature of this window, a full explanation of each configuration item can be obtained.  If the "Main Always On Top" box is checked, the Main MDBUS Window will always be on Top of all Windows for quick reference.  Unique Configurations can be kept via the Master/Slave Configuration-Database File (i.e. enter master1 for the File Ident. and press the Save File(s) button.  This file can be later recalled by entering master1 in the File Ident. edit box and pressing the Load File(s) button.

If the On menu item on the Main Window is invoked, MDBUS will begin polling the Slave.  The word after Comm. on the second line of the Main Window should be Nrml (steady).  If it is  Fail (steady), no successful communications is occurring.  If it alternates between Fail and Nrml, one or more of a Database type's configuration is wrong for the slave being polled.  To determine the problem, select Off on the Main Window.  Under the Display Menu, the various Windows for displaying the values for the different Data Types can be invoked.  If the Header line of a Window is displayed in Red, the data was not successfully retrieved.  The Configuration should now be checked to ensure that the number and start of the errant Data Type is correct.

The data retrieved from a Slave can be viewed by invoking the appropriate Window via the Displays menu item.  Any Data type with a number of zero will be grayed.  Communication statistics can be viewed by invoking the Statistics Menu item.  Statistics can be reset by Double clicking anywhere on the Statistics Window.  Transmitted and received messages can be viewed by selecting the Monitor Display.  Data in any Display Window can be viewed by using the scroll buttons, the page up/down keys, the cursor up/down/right/left keys, tab, and the ctrl home/end keys.  Any display window can be printed.  Clicking on the icon in the upper left-hand corner of a Display Window and selecting the Print item will do this.

Controls (Coil, Holding Register, Floats, and Longs) can be sent to the Slave by selecting the Control menu item.

Host Mode

In Master Mode, Mdbus is set up to poll one Slave.  However, Mdbus can be configured to poll multiple Slaves.  On the Main Mdbus Window is the Menu item "Host".  It is only enabled when Mdbus is Off.  Clicking on this item will bring up the Host Configuration Window.  There are 32 slots available for defining the File Ident. configuration of a Slave to be polled.  The Idents. must have been saved via the Main Configuration Window.  The Idents. could have been set up for 32 different Slaves or 32 different configurations for the same Slave or any combination.  Clicking on a slot will bring up a File Dialog for selecting the Ident. of a configuration to poll.  If the Cancel button is selected in the File Dialog instead of a configuration, the slot will be cleared.  A saved File used as an Ident. in the Host Configuration Window must be defined as Master, Normal type, and not have the Invalid CRC/LRC box checked.

If the "Prime" box is checked, the following parameters from the first configuration are used for polling all configurations:

Comm. Port, Fmt./Bd./Py., RTS/TX Delay, No Resp. T.O., Fail Try Count, Poll Delay, Excel DDE, Excel Sprdsht, DDE T.O., Macro DDE, Appl,Topic, and Macro.

If the “Excel DDE” box is checked, all data from all configurations will be dumped into Excel after all configurations are polled.  The first configuration's data goes into columns 1 to 6, the second's into columns 7 to 12, etc.

If the "Prime" box is unchecked, each configuration is standalone.  After a Poll, each configuration's data is dumped into the specified spreadsheet if the Excel DDE box is checked.

If the "One Scan" box is checked, only one poll of all configurations will be done and then Mdbus will turn Off automatically.

The “DCD Alerts” box has meaning only if an AT modem is being used for communicating with Slaves.  If the box is checked, Mdbus will produce an Alert Box and turn Off if DCD (Data Carrier Detect) is not obtained upon dial out or if DCD is lost after a successful dial out to a Slave.

When the "Poll Configurations" box is checked, Mdbus is now in Host Mode.  When Mdbus is turned On, The Host Control/Display Window will appear.  This window allows a configuration in the poll list to be selected.  Once a configuration is selected, data can be viewed from and controls can be sent to the selected configuration.

In Host mode, the configuration currently being polled is shown on the Main Window.

A particular configuration can be enabled or disabled from polling via DDE the poke commands HOSTENAB and HOSTDISB.  If the Host Window is shown, a disabled from polling configuration is shown in red.

Slave Mode

If MDBUS is configured as a SLAVE and the appropriate serial port is specified, it will respond to requests from a Master.  It responds to requests for the address contained in the Modbus Slave No. in the Configuration Window when the On menu item is invoked.  A Modbus Slave No. of 255 is a special case.  For this value, Mdbus will respond to all addresses received from a Master.  Data sent to the Master can be changed via a data display.  Double clicking on a point in a Data Display Window will bring up a Change Window for altering the value.  The Change Window also allows data values to be perturbed for a few scans or continuously for testing the way a Master responds to changes.  If the Control Menu item is selected, the Coil, Holding register, Floats, and Long Controls sent from a Master can be viewed in a Window.  The Control messages are tagged with the current time.

In Slave Mode, Mdbus can provide a simple Modbus Interface to another computer system via a serial interface.  Data to be sent by Mdbus can be supplied via DDE pokes by another application.  Up to 1000 values of one data type can be updated in Mdbus by the application with one DDE poke.

Monitor Mode

If MDBUS is configured for MONITOR mode, messages incoming on the RX line of a serial port can be viewed in Hex using RTU protocol and in ASCII using ASCII protocol.  Both TX and RX lines of a communications port can be monitored if they are diode coupled before being connected to the RX of the communications port configured to monitor.  Selective messages can be configured for viewing based upon Slave number, function code, and CRC errors.  Messages can also be logged to a capture file.  Please review “FIFO Notes” (click on Icon in mdbus folder) or Help on FIFO for information on detecting messages.

Taskbar Status Tray Area

The Main Window of Mdbus can be hidden.  If the right mouse button is clicked when the cursor is in the two-line status area of the Main Window, Mdbus will be reduced to an icon in the Taskbar Status area.  Passing the cursor over the Taskbar icon will display a line of status concerning Mdbus.  Clicking the right mouse button over the Mdbus icon in the Taskbar Status area will unhide Mdbus.  Clicking the left mouse button will bring up the display menu for selecting displays while Mdbus has been reduced to a Taskbar icon.  If Mdbus is hidden via a DDE command it cannot be unhidden except via a DDE command.

DDE

Mdbus in Master Mode can be easily set up to poke its data into an Excel SpreadSheet.  This includes all the Database values as well as Time and Poll Statistics.  Each Database type is stored in a column under a heading defining the Mdbus Instance and the type.    A cell with the word "End" terminates a column.  If the Heading includes a *, the data has not been successfully retrieved from the Slave.  To enable this feature, check the Excel DDE box and supply an Excel spreadsheet name in the Configuration Window.  When Mdbus has data to be sent to Excel, it will make a DDE connection to Excel.  Excel must be up and running with the specified spreadsheet.  In both Master and Slave mode, Mdbus can be made to turn On or Off via pokes from Excel or any other program supporting DDE pokes.  The Slave number and the Database points (start and number) can also be changed.  These changes are temporary and are not saved but remain in effect until Mdbus is closed.  Via pokes, Mdbus in Master Mode can be made to send out Coil, Holding Register, Floating Point, and Long Integer control commands.  Mdbus can execute a Macro in another application that supports DDE Execute.  Examples of supporting applications are Excel, Access, and Word for Windows.  Mdbus will also respond to DDE Requests for data.  Requested data can be Database values, time, polling statistics, and communication status.  Mdbus does not support DDE Hot Links.

For all poke/request commands the DDE application name is MDBUS, MDBUS0, MDBUS1, and MDBUS2 depending on the instances in use.  The DDE topic is always POKE.

A problem exists with the DDE connection between Mdbus and Excel when dumping data into Excel (Excel DDE box is checked) and also running an Excel macro (Macro DDE box is checked).  The spreadsheet that Mdbus dumps its data into should not be the first sheet on the sheet tab.

Mdbus can be made hidden via a DDE poke command.  When this happens, an icon is added to the Taskbar Status tray.  Moving the mouse cursor over the icon will produce a tooltip text box.  The text will indicate whether Mdbus is On or Off, its communication state, and the number of polls and errors.  Clicking the left mouse button will bring up a menu for display selection.  When Mdbus is unhidden, the Taskbar Status tray icon will be removed.

The following details the DDE POKE commands (Item and Data) which Mdbus will accept.

Item			Data		Meaning

STATE			ON		Turns Mdbus on

STATE			OFF		Turns Mdbus off

STATE			CLOSE		Closes out Mdbus

STATE			HIDE		Hides Mdbus(icon added to the Taskbar Status tray)

STATE			UNHIDE		Unhides Mdbus

SHCONF			ON		Brings up Mdbus Configuration Window

SLAVE			xxx		Sets Slave number to xxx (0 to 255)

PHONE			ATxxxxxxx	Sets Phone no. - must start with AT

STATISTICS		1		Clears Statistics

COIL yyy		x		Control Coil yyy to x (either 1 or 0) (Mdbus must be

ON in Master Mode)

COIL yyy		x,x,x 		Sets Coil yyy, yyy+1, etc. to x (either 1 or 0)

(Mdbus must be in Slave Mode)

HREG yyy		xxxx		Control Holding Reg. yyy to xxxx (+ or - 32767)

(Mdbus must be ON in Master Mode)

HREG yyy		xxxx,xxxx	Sets Holding Reg. yyy, yyy+1, etc. to xxxx (+ or –

32767)(Mdbus must be in Slave mode)

FLOA yyy		xxx.xxx 	Control Float yyy to xxx.xxx (Mdbus must be ON in

Master Mode)

FLOA yyy		xxx.xxx,xx.xx 	Sets Float yyy, yyy+1, etc. to xxx.xxx, xx.xx, etc.

(Mdbus must be in Slave Mode)

LINT yyy		xxx		Control Long yyy to xxx (+/- 2147483647) (Mdbus must

be ON in Master Mode or in Slave Mode)

LINT yyy		xxx,xxx		Sets Long yyy, yyy+1, etc. to xxx (+/- 2147483647)

(Mdbus must be in Slave Mode)

STAT yyy		x,x,x		Sets Status yyy, yyy+1, etc. to x (either 1 or

0)(Mdbus must be in Slave Mode)

IREG yyy		xxxx,xxxx,xxxx	Sets Input Reg. yyy, yyy+1, etc. to xxxx (+ or –

32767) (Mdbus must be in Slave mode)

NOCOIL			xxxx		Sets no. of Coils to xxxx

STCOIL			xxxx		Sets start no. of Coils to xxxx

NOSTATUS		xxxx		Sets no. of Status to xxxx

STSTATUS		xxxx		Sets start no. of Status to xxxx

NOIREG			xxxx		Sets no. of Input Regs. to xxxx

STIREG			xxxx		Sets start no. of Input Regs. to xxxx

NOHREG			xxxx		Sets no. of Holding Regs. to xxxx

STHREG			xxxx		Sets start no. of Holding Regs. to xxxx

NOFLOAT 		xxxx		Sets no. of F.P. Regs. to xxxx

STFLOAT 		xxxx		Sets start no. of F.P. Regs. to xxxx

NOLINT			xxxx		Sets no. of L.I. Regs. to xxxx

STLINT			xxxx		Sets start no. of L.I. Regs. to xxxx

AT212			ON		Enables 212 AT modem

AT212			OFF		Disables 212 AT modem

CONFIG			xxxxxxxx	Where xxxxxxxx is the File Ident. Config. to load.

xxxxxxx must have been previously saved via the

Configuration Window. (Mdbus must be OFF, and the

Configuration Window must be closed.)

HOST			ON		Turns Host mode on

HOST			OFF		Turns Host mode off

CONTROL 		xxxxxxxx	Where xxxxxxxx is the File Ident. configuration used

for Control and Display in Host mode.  xxxxxxx must

have been previously saved via the Configuration

Window. (Mdbus must be ON and in Host Mode.)

MUCO			ON		Sets function code 15 for Coil commands

MUCO			OFF		Sets function code 5 for Coil commands (default)

MUHR			ON		Sets function code 16 for H.R. commands

MUHR			OFF		Sets function code 6 for H.R. commands (default)

HOSTDISB		x		This disables a configuration from polling in Host

Mode.  x is the configuration slot to disable (0 to

31).

HOSTENAB		x		This enables a configuration from polling in Host

Mode.  x is the configuration slot to enable (0 to

31).

The following details the valid DDE REQUEST commands that Mdbus will accept.  Some request commands support multiple values.  In multiple value cases, commas separate the values.

Item			Meaning

TIME			Returns time in the following format dd-mmm-yyyy hh:mm:ss.

ONOF			Returns the state of Mdbus, either ON or OFF.

HOST			Returns the Host state of Mdbus, either ON or OFF.

MUCO			Returns the state of Coil function code 15, either ON or OFF.

MUHR			Returns the state of H.R. function code 16, either ON or OFF.

STTS x y		Returns Communication Statistics where x=1, 2, 3, or 4 for

Requests, Incompletes, CRC errors, No	Responses respectively and y

is the number to return.  If all are required, set x to 1 and y to

4.  If only requests are required, set x to 1 and y to 1.

COMM xxxx		Returns Communication state where xxxx is COIL, STAT, IREG, HREG,

FLOA, or LINK.  A 0 (comm. O.K.) or a 1 (comm. bad) is returned for

the database type selected.

COIL xxxx yyy		Returns the database values starting at Coil point xxxx.  The

values are 0 or 1.  yyy is the number of Coils requested.

STAT xxxx yyy		Returns the database values starting at Status point xxxx.  The

values are 0 or 1.  yyy is the number of Status requested.

IREG xxxx yyy		Returns the database values starting at Input reg. point xxxx.  The

values range from a maximum /minimum of + or - 32767.  yyy is the

number of Input registers requested.

HREG xxxx yyy		Returns the database values starting at Holding reg. point xxxx.

The values range from a maximum /minimum of + or - 32767.  yyy is

the number of Holding registers requested.

FLOA xxxx yyy		Returns the database values starting at Floating reg. point xxxx.

The values consist of a maximum of 15 digits.  yyy is the number of

Floating Point values requested.

LINT xxxx yyy		Returns the database values starting at Long Integer point xxxx.

The values are + or - 2147483647.  yyy is the number of Long

Integer values requested.

CMND			Returns the number of controls in the queue to be sent.  If this

number is 100 (the queue size), and controls are sent, they will

overwrite those currently in the queue.

This following is an example of an Excel spreadsheet showing the data that has been poked into it by Mdbus.

The following is an example of an Excel auto open macro used to start up Mdbus and obtain the DDE identification of Mdbus.

Dim channel

'

' auto open macro

'

Sub auto_open()

Shell ("c:\mdbus\mdbus.exe")				'start up mdbus

channel = DDEInitiate("mdbus", "poke")			'initiate dde channel to mdbus

End Sub

The following are examples of Excel macros used to poke commands into Mdbus.

'

'Turn Mdbus On

'

Sub mdbus_on()

DDEPoke channel, "state", "definitions!r3c1"     'turn mdbus on

End Sub

'

'Turn Mdbus Off

'

Sub mdbus_off()

DDEPoke channel, "state", "definitions!r4c1"     'turn mdbus off

End Sub

'

'Close Mdbus

'

Sub auto_close()

DDEPoke channel, "state", "definitions!r2c1"     'tell mdbus to close

DDETerminate channel                             'close dde channel to mdbus

End Sub

'

' set f.p. value

'

Sub set_fp()

Dim fpval

Dim fpno

fpno = Application.InputBox("Enter Floating Point Register No.", "Floating Point Change", , , , , , 2)

fpval = Application.InputBox("Enter Floating Point Register value", "Floating Point Change", , , , , , 1)

Worksheets("definitions").Cells(2, 2).Value = fpval

DDEPoke channel, "FLOA " + fpno, "definitions!r2c2"   'set f.p. value

End Sub

'

' set coil value

'

Sub set_coil()

Dim coilval As Integer

Dim coilno

coilno = Application.InputBox("Enter Coil Point No.", "Coil Change", , , , , , 2)

coilval = Application.InputBox("Enter Coil value (either 0 or 1)", "Coil Change", , , , , , 1)

Worksheets("definitions").Cells(3, 2).Value = coilval

DDEPoke channel, "COIL " + coilno, "definitions!r3c2"   'set coil value

End Sub

'

' set holding register value

'

Sub set_hr()

Dim hrval As Integer

Dim hrno

hrno = Application.InputBox("Enter Holding Register Point No.", "Holding Register Change", , , , , , 2)

hrval = Application.InputBox("Enter Holding Register value (+ or - 32767)", "Holding Register Change", , , , , , 1)

Worksheets("definitions").Cells(4, 2).Value = hrval

DDEPoke channel, "HREG " + hrno, "definitions!r4c2"   'set holding register value

End Sub

'

' Set Slave Address to value in definitions sheet row 5 column 1

'

Sub set_slave()

DDEPoke channel, "slave", "definitions!r4c1"     'set slave address

End Sub

'

' Miscellaneous Sample Initialization

'

Sub misc_init()

mdbus_off                                       ' turn mdbus off

DDEPoke channel, "slave", "definitions!r2c5"    'set slave address to 3

DDEPoke channel, "nocoil", "definitions!r3c5"   'set no. of coils to 5

DDEPoke channel, "stcoil", "definitions!r4c5"   'set start coil to 2

DDEPoke channel, "nostatus", "definitions!r5c5" 'set no. of status to 11

DDEPoke channel, "ststatus", "definitions!r6c5" 'set start status to 3

DDEPoke channel, "noireg", "definitions!r7c5"   'set no. of status to 12

DDEPoke channel, "stireg", "definitions!r8c5"   'set start status to 4

DDEPoke channel, "nohreg", "definitions!r9c5"   'set no. of status to 13

DDEPoke channel, "sthreg", "definitions!r10c5"  'set start status to 5

DDEPoke channel, "nofloat", "definitions!r11c5" 'set no. of status to 14

DDEPoke channel, "stfloat", "definitions!r12c5" 'set start status to 6

DDEPoke channel, "phone", "definitions!r13c5"   'set phone no. to atdt-403-555-1212

DDEPoke channel, "statistics", "definitions!r14c5" 'clear statistics

mdbus_on                                        'turn mdbus on

End Sub

'

' Load Test Configuration

'

Sub load_test()

mdbus_off                                       'turn mdbus off

DDEPoke channel, "config", "definitions!r6c1"   'load configuration test

mdbus_on                                        'turn mdbus on

End Sub

The following is an example of an Excel macro used to set up the Control Configuration.  This is required for all Control from Excel in Host mode.

'

' Set Host Control/Display Configuration

'

Sub control_display()

DDEPoke channel, "control", "definitions!r6c1"   'Set Host Control/Display

End Sub

The following are examples of Excel macros used to request data from Mdbus.  Please note that for these examples to work, you must have at least 20 holding registers starting at 1 and 15 coils starting at 1 configured in Mdbus.

'

' request holding reg. macro

'

Sub request_hreg()

Dim datamg

Dim i As Integer

datamg = DDERequest(channel, "hreg 1 20")     'get data array from mdbus

For i = LBound(datamg) To UBound(datamg)

Worksheets("data request").Cells(i + 1, 1).Formula = datamg(i)  'xfer data to data request

Next i

End Sub

'

' request coils macro

'

Sub request_coil()

Dim datamg

Dim i As Integer

datamg = DDERequest(channel, "coil 1 15")     'get data array from mdbus

For i = LBound(datamg) To UBound(datamg)

Worksheets("data request").Cells(i + 1, 2).Formula = datamg(i)  'xfer data to data request

Next i

End Sub

The following details the values from the definitions spreadsheet used in the previous Excel macros.

The following is an example of Excel macro that can be called from Mdbus.

'

' test_beep

'

Sub test_beep()

Beep

End Sub

The following portion from the Configuration Window shows that data will be poked into an Excel Workbook test.xls and Worksheet scada and an Excel macro called test_beep will be executed.  Different language versions of Excel abbreviate row and column with different letters than R and C.  For instance, the French version of Excel uses letters L and C, the German version uses letters Z and S, and the Spanish version uses letters F and C.  Mdbus needs this information to successfully poke data into an Excel spreadsheet.  The French version of Excel requires [test.xls]scada,1, the German version of Excel requires [test.xls]scada,2, the Spanish version of Excel requires [test.xls]scada,3 and the Dutch version of Excel requires [test.xls]scada,4 instead of [text.xls]scada (English default) in the Excel Sprdsht edit box.

The following portion from the Configuration Window shows that data will be poked into an Excel Workbook test.xls and Worksheet scada and an Access macro called macro1 will be executed in the database db1.mdb.  Note that the database extension is not used.

The following portion from the Configuration Window shows that data will be poked into an Excel Workbook test.xls and Worksheet scada and a Word macro called macro1 will be executed in the document doc1.doc.

For technical support or suggestions for future enhancements, please contact

Calta Computer Systems Limited

Suite 230, 550 - 71st Ave. S.E.

Calgary, Alberta, Canada  T2H 0S6

Phone		- 403-252-5094

Fax		- 403-252-5102

E-mail		- ccompute@calta.com

Web Site	- http://www.calta.com/